©2025 Rolls-Royce SMR Ltd

The information in this document is proprietary and confidential to Rolls-Royce SMR and is available to authorised recipients only – copying and onward distribution is prohibited other than for the purpose for which it was made available.

Rolls-Royce SMR RO Resolution Plan

| RO unique Number: | RO-RRSMR-009 |
| --- | --- |
| RO Title: | RO-RRSMR-009 Safety Case for Hydrogen Management in Severe Accidents |
| Lead Technical topic: | Severe Accident Analysis |
| Related Technical topic(s): | Chemistry Civil Engineering Control & Instrumentation Electrical Engineering Fault Studies Internal Hazards Mechanical Engineering Structural Integrity |

## Regulatory Observation

Combustible gases can be generated during accident scenarios of pressurised water reactors (PWRs). These gases are generated via various mechanisms, including rapid oxidation of metals around the reactor core area, slower oxidation of remaining metals, radiolysis of water, and molten concrete corium interactions. These gases have the potential to undergo various combustion modes that can challenge the containment and the equipment and structures within. The rate and concentration of such gases is a function of the specific accident scenario, but can be most challenging for those faults that lead to core degradation.

## Hydrogen generated during faults can migrate from the reactor to the containment atmosphere. The route and mode of transport is dependent on the state of the primary circuit and accident scenario. The resulting distribution of hydrogen in the containment is governed by various physical phenomena, including: inertial drivers, diffusion, mass and heat transfer. Typically, early in the release, there is a high degree of non-uniformity in hydrogen distribution as it is initially entrained in the release of steam from the primary circuit. Later in the transient, buoyancy driven forces may dominate flows. In the later phases of the accident, hydrogen can stratify in upper regions of compartments. When uniformly distributed, due to the nature of the PWR environment, the risk of high energy combustion modes that will challenge the containment is widely accepted to be low. However, during phases of non-uniform distribution, there is a raised the potential for localised combustion, which can impinge on nearby structures systems and components (SSCs) and potentially propagate with more severe and widespread consequences.

## The Rolls-Royce Small Modular Reactor (RR SMR) is a PWR that employs in-vessel retention (IVR) as its core melt mitigation strategy. As such, hydrogen generated during core degradation that is released from the primary circuit poses the most significant risk for combustion. Therefore, sequences with core melt inform the design basis for hydrogen mitigation strategies. To meet this demand, the RR SMR employs the hydrogen reduction system (HRS) [JMT] (Ref. [1]).

## To date, the RP has submitted analysis of loads from global slow deflagration (Ref. [2]) (i.e. considering uniform distribution). In addition, the RP has identified limiting scenarios that lead to conditions in which localised flame acceleration and detonation criteria are met which require further detailed analysis. The analyses have been performed using the MAAP5 and GOTHIC codes and are based on an evolving design iteration, with a rational for why future design iterations will not undermine the findings.

## The RP has also set out a high-level methodology for performing detailed combustion analysis, and how the output of the analysis will be utilised. This includes a high level description of how the output will interface with the structural integrity topic area. The methodology outlines two potential calculation routes for performing detailed combustion analysis, one using GASFLOW-MPI, and another using FLACS-CFD.

## Currently, design development work and substantiation of the HRS [JMT] is underway, with an aim of delivering outputs of combustion analysis during GDA timescales. However, there are uncertainties in how the safety case will utilise combustion analysis to demonstrate that the RR SMR plant design can effectively mitigate the release of hydrogen during severe accidents, and which combustion code will be used to provide this evidence. There is also uncertainty in the scope of deterministic analysis, and design substantiation, used to support the evolution of the HRS [JMT] design.

Relevant Legislation, Standards and Guidance

The following SAPs (Ref. [3]) are most relevant to this Regulatory Observation:

FA.15 – “Fault states, scenarios and sequences beyond the design basis that have the potential to lead to a severe accident should be analysed.”

A systematic approach should be taken to identify scenarios for severe accident analysis. Scenarios should not be screened on frequency alone, and analysis should be performed on a best estimate basis unless uncertainties warrant applying conservatism. The analysis should demonstrate the absence of cliff edge effects, and consider the potential failure of barriers to release.

FA.16 – “Severe accident analysis should be used in the consideration of further risk-reducing measures.”

The SAA should be used to identify any further reasonably practicable safety features and form the basis for accident management strategies and procedures. Any identified SSCs should be qualified to operate in the conditions in which it is required to perform safety functions.

AM.1 – “Strategies and plans should be in place to prepare for and manage accidents at the facility and/or site.”

Accident management strategies should be based on the SAA with the primary goal of preventing failure of barriers to release. The strategies should consider long-lasting events where external access to site may not be possible. The SAA should identify all human actions required and enable the development of severe accident management guidelines (SAMGs). The strategies should include the provision of appropriately robust, suitable and sufficient instrumentation for monitoring the facility and site in accident conditions to enable enaction of SAMGs, decision making, and record important parameters.

AV.1 – AV.6 – ONR expects:

- Computer codes adequately reflect theoretical models.

- Codes/models are validated for intended use.

- Assumptions and user inputs are well founded.

- Models and datasets are developed and calculations are performed in accordance with appropriate quality management procedures.

- Verification and validation, and code manuals should be documented.

- Sensitivity analysis should be performed.

ONR’s Technical Assessment Guide for Severe Accident Analysis (Ref. [4]) also provides guidance. It states that phenomena that could challenge technical safety criteria should be identified, appropriate safety measures should be determined to prevent or mitigate these phenomena, and their effectiveness should be demonstrated.

IAEA’s guidance also specifically discusses risks posed from hydrogen:

SSG-2 – para 3.56 (Ref. [5]) – sequences that have the potential to lead to containment failure due to explosion of combustible gases should be practically eliminated.

SSG-88 – Para I-21 (Ref. [6]) - Dedicated means to prevent the generation of hydrogen and its accumulation at critical concentrations, and to eliminate hydrogen detonation, are needed at all nuclear power plants, although different means are preferred for different plant designs.

Regulatory Expectations

For Gen-III/III+ reactors, such as the RR SMR, IAEA’s SSG-88 (Ref. [6]) lays out expectations that designers/vendors demonstrate that severe accident sequences that could lead to containment failure have a low predicted frequency to a high degree of confidence (i.e. practically eliminated). For hydrogen risk, ONR, therefore, expect that safety features are provided to prevent high energy combustion modes that could lead to containment failure, and their effectiveness is demonstrated. ONR does not, however, have specific expectations related to the means of mitigation/prevention.

In pursuit of this demonstration ONR expect that technical criteria are determined, and shown to be effective through deterministic analysis. ONR also expect that appropriate computer codes and models are used in this demonstration. Due to limitations of integral codes in modelling localised phenomena, this demonstration is often provided using computational fluid dynamics codes. These codes and models should be demonstrated to be adequately validated for their specific use.

ONR also expect that the deterministic analysis is used to inform the design of SSC. This includes capacity and locations of SSCs for hydrogen removal, appropriate containment layout to promote mixing, as well as monitoring. ONR expects that where claims are made against adequate mixing, hydrogen removal and hydrogen monitoring, that appropriate analysis supports those claims. If uncertainty remains in the detailed design, ONR expect that sufficient sensitivity analysis is performed to demonstrate that all cases envelope a future refined design.

Whilst severe accident management guidelines are not expected to be produced for generic design assessment, it is expected that the design enables mitigatory actions that could be taken to further reduce risks. For severe accident scenarios, operation of certain mitigation strategies have the potential to worsen conditions for hydrogen. For example, condensation of steam can increase the volumetric concentration of hydrogen. Situational awareness is therefore key to informing an operators decision making (e.g. initiation of containment spray). ONR therefore expect that the design of monitoring systems is adequate to enable those decisions, and that, if appropriate, sensitivity analysis is performed to demonstrate that no mitigatory actions can lead to scenarios that would challenge the containment.

ONR also expect that SSCs claimed to function during severe accidents are adequately qualified for the environmental conditions. In the context of hydrogen, this means that any heat and pressure loads generated from hydrogen combustion or recombination are considered in the qualification of containment, supporting structures, monitoring equipment, and any other safety features which are credited for severe accident mitigation.

## Regulatory Observation Actions and Resolution Plan

RO-RRSMR-009.A1 – Systems Definition

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should: Provide a system definition of the HRS [JMT] and Containment System [JMA].

The following information should be provided:

- The technology type employed

- Design substantiation of those technologies

- The number of ignitors and passive autocatalytic recombiners (PARs), their location within the containment and capacity, linking the rationale to deterministic analysis

- The number and location of hydrogen monitors, linking the rationale to deterministic analysis

- Details of any associated power sources and I&C

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A1

As part of the resolution plan for RO-RRSMR-009.A1, information will be provided within the safety case as follows:

A description of the HRS [JMT] and Containment System [JMA] is provided within the documentation listed below and summarised within Chapter 6 of the E3S case [11].

- A description of the Hydrogen Reduction System [JMT] is reported within the Hydrogen Reduction System [JMT] SDD [7] this includes:

  - The technology types employed.

  - Design substantiation based on analysis performed to date.

  - The number of ignitors and passive autocatalytic recombiners (PARs), linking the rationale to deterministic analysis.

  - The approximate location of ignitors and PARs with associated rationale for positioning.

    - Analysis which demonstrates insensitivity of the HRS [JMT] performance to precise positioning is presented within the Hydrogen Reduction System [JMT] SDD [7]. Containment gas mixing analysis using GOTHIC shows that precise PAR location has little impact on their performance [7]. Approximate ignitor locations are defined, and assessments of ignition criteria from these locations is not sensitive to the exact location.

    - The precise location of PARs and ignitors within the containment layout [20] [21] will be included prior to site licensing.

  - The number and viable locations of hydrogen monitors, linking the rationale to deterministic analysis.

  - Details of any associated power sources and I&C.

- A description of the Containment System [JMA] is reported within the Containment System [JMA] SDD [9] this includes:

  - The technology types employed.

  - Design substantiation. The JMA SDD will contain design substantiation, largely associated with the free air volume.

  - Details of any associated power sources and I&C (briefly).

- In addition, design substantiation for the Containment Vessel [PT250] is included within the Component Substantiation Report [17]. A verification strategy for the Containment System [JMA] is provided [10].

- The Containment Layout RD10 and DR3 baseline model is due to be issued in Dec 2025 [20] and Sep [21] respectively. This will show that there are no “compartments” within containment.

RO-RRSMR-009.A2 – Demonstration of the Effectiveness of Safety Features

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should:

- Demonstrate that the limiting cases for high energy combustion modes have been identified

- Define and justify suitable acceptance criteria for avoidance of high energy combustion leading to challenges to containment

- Define and justify suitable acceptance criteria for containment loads

- Demonstrate that acceptance criteria are met for limiting cases

- Perform sensitivity analysis to demonstrate no cliff-edge effects associated with unavailability of SSCs and with correct performance of other SSCs that can impact HRS [JMT] performance.

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A2

As part of the resolution plan for RO-RRSMR-009.A2, information will be provided within the safety case as follows:

The effectiveness of relevant safety features for the most limiting hydrogen scenarios within DEC-B (applicable to the SA CSM [JM02] [23]) will be considered within the documentation listed below, in addition, Chapter 6 and Chapter 15 of the E3S case [11] [13] capture the safety case position.

- Demonstration that the limiting cases for high energy combustion modes have been identified can be found within the SA Hydrogen Management Report [1], refined information with respect to the latest design iteration will be provided in Issue 2 of the SA Hydrogen Management Report (due to be issued in Jan 2026) [12]. Limiting cases for high energy combustion modes will also be discussed within the SAA Summary Report [14] (due to be issued in Feb 2026). Further information justifying the design position at RD10 (expected to be DRP5) will be provided in Issue 3 of the SA Hydrogen Management Report [26] (due to be issued in Dec 2026). It is expected that new assessments would be limited, and qualitative arguments will be used for minor design revisions. Recommended further work from Issue 2 will also be addressed in Issue 3.

- Technical and radiological acceptance criteria are defined within the Plant States Module in DOORS [16]. Suitable acceptance criteria for avoidance of high energy combustion leading to challenges to containment are presented in the SAA methodology report [15], with further evidence supporting justification due to be presented in [12]. These will be used to update the Plant States Module in DOORS [18].

- Acceptance criteria for static containment loads are defined and justified within the SAA Methodology report [15]. An initial approach for deriving a reference level for loading relevant to energetic combustion modes (i.e. dynamic loads) will also be defined, and justified with guidance from structural integrity experts in Issue 2 of the SA Hydrogen Management Report [12]. This approach will use existing information from bounding internal hazards assessments. Further quantification of acceptance criteria, and comparison against limiting loadings will be provided in Issue 3 of the SA Hydrogen Management Report [26] (due Dec 2026).

- Demonstration that acceptance criteria are met for limiting cases will be provided within Issue 2 of the SA Hydrogen Management report [12], with a summary of analyses provided in Issue 3 of the SAA Summary Report [14].

- Sensitivity analysis to demonstrate no cliff-edge effects are associated with unavailability of SSCs and with correct performance of other SSCs that can impact HRS [JMT] performance will be provided within Issue 2 of the SA Hydrogen Management Report [12]. Recommended further work from Issue 2 [12] will also be addressed in Issue 3 of the SA Hydrogen Management Report [26].

RO-RRSMR-009.A3 – Demonstration of Effective Mixing

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should:

- Demonstrate the containment [JMA] and HRS [JMT] design promotes mixing to avoid localised build up of hydrogen where this is claimed within the safety case

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A3

As part of the resolution plan for RO-RRSMR-009.A3, information will be provided within the safety case as follows:

- The effectiveness of mixing is presented within Version 3 of the E3S case, adequate mixing of hydrogen is discussed within Chapter 6 of the E3S Case [11].

- Demonstration that the containment [JMA] and HRS [JMT] design promotes mixing to avoid localised build-up of hydrogen is provided within Section 4.6 of the HRS [JMT] SDD [7], and further details will be summarised within Issue 2 of SA Hydrogen Management Report [12].

RO-RRSMR-009.A4 – Demonstration of Optimised Hydrogen Monitoring

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should:

- Demonstrate that sufficient hydrogen monitoring exists and is adequately located to provide situational awareness and inform decision making.

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A4

As part of the resolution plan for RO-RRSMR-009.A4, information is provided within the safety case as follows:

- Hydrogen monitoring is described within Chapter 6 of the E3S case [11], in addition to guidelines on the use of the spray system.

- Demonstration that sufficient hydrogen monitoring exists and is adequately located to provide situational awareness and inform decision making is provided within the HRS [JMT] SDD [7].

RO-RRSMR-009.A5 – Demonstration of Equipment Qualification

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should:

- Identify SSCs that may be impacted by localised combustion or heat loads from recombiners

- Determine qualification parameters for impacted SSCs

- Demonstrate the withstand of containment structures against localised loads

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A5

SSCs that are credited with a safety function during severe accidents may be subject to localised loads from hydrogen combustion or recombination. As part of the resolution plan for RO-RRSMR-009.A5, information will be provided within the safety case as follows:

- SSC that could be impacted by local loads have initially been identified in the SAC [JM02] Safety Measure Design Specification (SDS) [30]. The SA Hydrogen Management Report [12] will provide an updated list of SSC that may be impacted by hydrogen combustion or recombination.

- The loads experienced by SSCs are derived from Severe Accident Analysis (SAA). The SA Hydrogen Management Report [12] will provide the analytical basis for determining the loads applicable to the identified SSCs located within discretised regions of containment. For a given location, an estimate of the expected peak loading, timing of loading (with respect to SSC mission time), and duration of loading will be derived using information available from existing assessments. Engineering judgement will be applied to provide information on loadings where explicit assessments are not available (e.g. where a coarse modelling approach does not derive information throughout containment). This includes the assessment of thermal and dynamic pressure loads on containment structures. It is acknowledged that not all SSC withstand information will be available for the initial review to be presented in Issue 2 of the SA Hydrogen Management Report [12].

- An illustrative comparison will be made for the containment structures between the bounding DEC-B loads from energetic combustion modes (i.e dynamic loads) and the relevant acceptance criteria (see Response 3) in the SA Hydrogen Management Report [12]. Available information on SSC withstand will be utilised where available.

- Further comparison for SSC with limited information at Issue 2 of the SA Hydrogen Management Report [12], and refined loading information, will be provided in Issue 3 of the SA Hydrogen Management Report [26] (due Dec 2026).

- DEC-B conditions in general are not expected to exceed DB Internal Hazards Loads. If DEC-B loads are bounding, the identified loads will be defined as withstand and/or operational requirements on SSC. RR-SMR will communicate its EQ arrangements along with demonstrating the application of those arrangements, within the deliverables that form the RO-RRSMR-012 Resolution Plan [22].

- Where additional substantiation or analysis is required, this will be identified as further work in SA Hydrogen Management Report [12].

RO-RRSMR-009.A6 – Demonstration of Validation of Methods

In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should:

- Demonstrate that the model employed adequately represents the final reference design, or that sensitivity studies envelope uncertainty in the design.

- Provide relevant phenomena importance ranking tables (PIRTs) and Test Assessment Matrices (TAMs)

- Perform sensitivity studies and/or incorporate conservatism to account for uncertainties in the modelling.

Rolls-Royce SMR Ltd. Resolution Plan for RO-RRSMR-009.A6

As part of the resolution plan for RO-RRSMR-009.A6, information will be provided within the safety case as follows:

The demonstration of validation of methods will be reported within the documentation listed below, in addition, this will be summarised within Chapter 15 of the E3S case [24].

- Demonstration that the model employed adequately represents the reference design:

  - The SA Hydrogen Management Report Issue 2 [12] will present the results of sensitivity studies examining the impact of significant containment layout design changes from DRP2 (Reference Design 8) to DRP4 (Reference Design 9 plus additional design changes to align with Version 3 of the E3S Case). This will focus on the changes to the Steam Generator compartments and the impact on gas mixing, and likelihood of energetic combustion.

  - It is anticipated that the final design position for GDA will be DRP 5, which is expected to include Reference Design 10. A qualitative assessment of design changes, and their impact on analyses, between DRP4 and DRP5 will be presented in Issue 3 of the SA Hydrogen Management Report [26]. It is assumed that containment layout design modifications will be minor, and will not require re-assessment.

  - A review of residual uncertainty in the design position, in comparison to code capability in representing detailed design aspects, uncertainty in methods, and applied conservatisms will be included in the Severe Accident Analysis Verification, Validation and Uncertainty Quantification Summary Report (due in Feb 2026) [25]. A qualitative judgement will be made on the relative importance of different sources of uncertainty on analysis outputs and their use in safety case arguments, which will be used to guide further refinements in the methods used and support a maturing analysis position for Issue 3 of the SA Hydrogen Management Report [26].

- Demonstration of validation of analysis methods:

  - The RR SMR thermal hydraulic Verification, Validation and Uncertainty quantification (VVUQ) process requires the development of Phenomena Identification & Ranking Tables (PIRTs) and Test & Assessment Matrices (TAMs) for analysis methods utilised. A PIRT for phenomena related to detailed localised gas mixing and hydrogen combustion is in development [27]. This will provide a detailed review of phenomena related to gas mixing in containment, and rank the importance of phenomena in relation to an accident scenario and key figures of merit required to predict the possibility of energetic hydrogen combustion. In addition, a detailed review of phenomena relevant to hydrogen combustion, including energetic combustion modes will be produced and their importance ranked according to key figures of merit relevant to the possibility of energetic combustion and the resultant overpressure.

  - Corresponding TAMs for the use of the GOTHIC code (3D gas mixing and ignition/slow deflagration analysis) [28] and FLACS-CFD (energetic combustion analysis) [29] are in development. These will review code capability, validation evidence, and uncertainty, with respect to the phenomena of importance. It is anticipated that the reviews will lead to the identification of further work to improve validation evidence.

  - A validation summary is also in development for GASFLOW-MPI (3D gas mixing and combustion analysis), however the objective is not to use GASFLOW-MPI for safety case analysis but it will support code to code comparisons. The validation summary will review available validation evidence for the GASFLOW-MPI code, and compare these to a limited selection of phenomena of importance (from [27]) to form a judgement on the code capability. Extensive details typically included in a TAM review such as code formulation and performance in domains of interest will not be included. The validation summary will be provided as an appendix to the Severe Accident Analysis Verification, Validation and Uncertainty Quantification Summary Report (due in Feb 2026) [25].

  - The outcome of the PIRT/TAMs ([27], [28], [29]), and validation summary will be summarised within [25], and individual documents will be available for sampling from February 2026. Identification of key tasks to improve the validation status of analysis methods will also be documented within [25], however resolution of all proposed tasks will not be expected within GDA timescales.

  - Code comparisons between GOTHIC and GASFLOW-MPI gas mixing predictions, and FLACS-CFD and GASFLOW-MPI combustion predictions will be presented as appendices to the Severe Accident Analysis Verification, Validation and Uncertainty Quantification Summary Report (due in Feb 2026) [25]. These comparisons will support justification for the use of the GOTHIC/FLACS-CFD codes to generate safety case evidence.

- Sensitivity studies and/or conservatism to account for uncertainties in the modelling approach will be described within the SA Hydrogen Management Report (due to be issued in Jan 2026) [12].

## Schedule

Impacted Submissions

The table below lists the submissions on the Master Document Submission List (MDSL) that will be impacted through resolution of this RO, and how they will be impacted. Note further additional documents may be identified from the workshops and work carried out as described above.

| Existing GDA Submission | Impact |
| --- | --- |
| SA Hydrogen Management Report [12]. | This report will include: - Demonstration that the limiting cases for high energy combustion modes have been identified. - Justification of suitable acceptance criteria for avoidance of high energy combustion leading to challenges to containment. - Initial derivation of dynamic loading limits for DEC-B. - Demonstration that acceptance criteria are met for limiting cases. - Sensitivity analysis to demonstrate no cliff-edge effects. - Demonstration that the containment [JMA] and HRS [JMT] design promotes mixing to avoid localised build-up of hydrogen. - Qualification parameters for impacted SSCs. - Inclusion of sensitivity studies/conservatism to account for uncertainties in the modelling. - Sensitivity studies to envelope uncertainty in the design. - A description of sensitivity studies and conservatism used to account for uncertainties in the modelling. |
| SA Hydrogen Management Report [26]. | This report will include: - Further information justifying the design position at RD10 (expected to be DRP5). |
| SAA Summary Report [14]. | This report will: - Summarise the limiting cases for high energy combustion modes. - Demonstration that acceptance criteria are met for limiting cases. |
| Chapter 3 of the E3S case [19]. | This report includes a summary of the overarching EQ methodology and governing principles |
| Chapter 6 of the E3S case [11]. | This report provides: - A summary of the HRS [JMT] and Containment System [JMA]. - A discussion on the adequate mixing of hydrogen. - A description of hydrogen monitoring, in addition to guidelines on the use of the spray system. - Discussion of the EQ verification strategy. |
| Chapter 15 of the E3S case [13]. | This report provides: - A summary of validation of methods. - The safety case position for the effectiveness of relevant safety features for the most limiting hydrogen scenarios within DEC-B. |
| Chapter 15 of the E3S case [24]. | This report will provide: - An updated summary of the demonstration of validation of methods for hydrogen analysis. |
| The Containment System [JMA] SDD [9]. | JMA SDD will provide system definition. |
| Containment Layout RD10 baseline model [20] [21]. | This report will show that there are no “compartments” within containment. |
| Plant States Module in DOORS [18]. | Will be updated to include acceptance criteria derived in the SAA methodology report [15]. |
| Severe Accident Analysis Verification, Validation and Uncertainty Summary Report [25]. | This report will: - A discussion of uncertainties associated with the design and analysis methods deployed, and reference to sensitivity studies performed. - Summary of relevant PIRTs (including PIRT for detailed localised gas mixing and hydrogen combustion phenomena) - Summary of relevant TAMs (including TAMs for GOTHIC, FLACS-CFD and validation summary for GASFLOW-MPI) Code comparisons between GOTHIC and GASFLOW-MPI gas mixing predictions, and FLACS-CFD and GASFLOW-MPI combustion predictions |
| Test and Assessment Matrix (TAM) for Containment Hydrogen Combustion Analysis using FLACS-CFD Hydrogen Combustion Assessments [29] | This will provide a review of code capability, validation evidence, and uncertainty, with respect to the phenomena of importance. |
| Test and Assessment Matrix (TAM) for Containment Gas Mixing Analysis using GOTHIC [28] | This will provide a review of code capability, validation evidence, and uncertainty, with respect to the phenomena of importance. |
| A PIRT for phenomena related to detailed localised gas mixing and hydrogen combustion [27] | This will provide a detailed review of phenomena related to gas mixing in containment, and hydrogen combustion, and rank the importance of phenomena. |

## References

[1] System Design Description for the Hydrogen Reduction System, SMR0006184, Issue 2, Rolls-Royce SMR Ltd., March 2024

[2] Severe Accident Hydrogen Management Report, SMR0016108, Issue 1, Rolls-Royce SMR Ltd., January 2025

[3] ONR, Safety Assessment Principles for Nuclear Facilities, 2014 Edition, Revision 1, January 2020

[4] Severe Accident Analysis, NS-TAST-GD-007, Revision 5.1, December 2022

[5] Deterministic Safety Analysis for Nuclear Power Plants, Specific Safety Guide, No SSG-2. Rev. 1. 2019

[6] Design Extension Conditions and the Concept of Practical Elimination in the Design of Nuclear Power Plants, Specific Safety Guide, No. SSG-88, Rev. 1, 2024

[7] System Design Description for the Hydrogen Reduction System [JMT], SMR0006184, Issue 4, Aug 2025.

[8] Verification Strategy for the Hydrogen Reduction System [JMT], SMR0017891, Issue 1, June 2025.

[9] Containment [JMA] System Design Description, SMR0005089, Issue 2, Sep 2025.

[10] Verification Strategy for the Containment System [JMA], SMR0017986, Issue 1. March 2025.

[11] Environment, Safety, Security and Safeguards Case Version 3, Tier 1, Chapter 6: Engineered Safety Features, SMR0003771, Aug 2025.

[12] SA Hydrogen Management Report, SMR0016108, Issue 2, due to be issued Jan 2026.

[13] Environment, Safety, Security and Safeguards Case Version 3, Tier 1, Chapter 15: Safety Analysis, SMR0003977, Aug 2025.

[14] SAA Summary Report, SMR0006219, Issue 3, due to be issued Feb 2026.

[15] Severe Accident Analysis Methodology, SMR0006141, Issue 4, Aug 2025.

[16] FS (Fault Schedule), SM (Safety Measures) and Plant States DOORS Module Extracts, SMR0004916, Issue 3, Feb 2025.

[17] Containment Vessel [PT250] Component Substantiation Report, SMR0024948, Issue 1, Aug 2025.

[18] FS (Fault Schedule), SM (Safety Measures) and Plant States DOORS Module Extracts, SMR0004916, Issue 5, Nov 2026.

[19] Environment, Safety, Security and Safeguards Case Version 3, Tier 1, Chapter 3: E3S Objectives and Design Rules for SSCs, SMR0004589, Aug 2025.

[20] Containment [UJA] RD10 Model Baseline, SMR0008838, Issue 3, due to be included as part of the Reactor Island Federated Navisworks model, SMR0005255, Issue 4, available for sampling from Dec 2025.

[21] Reactor Island Federated Navisworks model, SMR0005255, Issue 5, available for sampling from Sep 2026.

[22] Rolls-Royce SMR RO Resolution Plan RO-RRSMR-012, Equipment Qualification Arrangements and Demonstration, SMR0026976/002, Sep 2025.

[23] Safety Measure Design Description for the Severe Accident Containment [JM02] Safety Measure, SMR0021874, Issue 2, Aug 2025.

[24] Environment, Safety, Security and Safeguards Case Version 4, Tier 1, Chapter 15: Safety Analysis, SMR0003977, due to be issued June 2026.

[25] Severe Accident Analysis Verification, Validation and Uncertainty Quantification Summary Report, Issue 1, due to be issued Feb 2026.

[26] SA Hydrogen Management Report, SMR0016108, Issue 3, due to be issued Dec 2026.

[27] Phenomena Identification and Ranking Table (PIRT) for Containment Gas Mixing and Hydrogen Combustion Analysis, SMR0027379, Issue 1, available for sampling from Feb 2026

[28] Test and Assessment Matrix (TAM) for Containment Gas Mixing Analysis using GOTHIC, SMR0027378, Issue 1, available for sampling from Feb 2026

[29] Test and Assessment Matrix (TAM) for Containment Hydrogen Combustion Analysis using FLACS-CFD Hydrogen Combustion Assessments, TBC document number, Issue 1, available for sampling from Feb 2026

[30] Safety Measure Design Specification for the Severe Accident Containment [JM02] Safety Measure, SMR0016598, Issue 1, April 2025

## Record of Change

| Date | Revision Number | Reason for Change |
| --- | --- | --- |
| 07/07/2025 | 1 | First Issue |
| 07/08/2025 | 2 | Second issue to incorporate ONR comments |
| 07/08/2025 | 3 | Up issue to correct inconsistency in Action 1 text |
| 05/12/2025 | 4 | Up issue addressing final comments received from the ONR. |

## Approvals

| Author | Sign | Print | Role | Date |
| --- | --- | --- | --- | --- |
|  | See Teamcenter | {REDACTED} | {REDACTED} | See Teamcenter |
| Reviewer | Sign | Print | Role | Date |
|  | See Teamcenter | {REDACTED} | {REDACTED} | See Teamcenter |
|  | Sign | Print | Role | Date |
| Reviewer | See Teamcenter | {REDACTED} | {REDACTED} | See Teamcenter |