| GDA Regulatory Observation |  |
| --- | --- |
| REGULATOR TO COMPLETE |  |
| RO unique no.: | RO-RRSMR-013 |
| Revision: | 2 |
| Date sent: | 06/08/25 |
| Acknowledgement required by: | 28/08/25 |
| Resolution Plan Agreement Required by: | 25/09/25 |
| Record Reference: | ONRW-2126615823-8255 |
| Related RQ / RO No. and CM9 Ref: (if any): | RO-RRSMR-009 |
| Observation title: | Consideration of chemistry effects during severe accidents |
| Lead technical topic: Chemistry | Related technical topic(s): Fault Studies Probabilistic Safety Analysis Radiological Consequences Severe Accident Analysis |
| REGULATORY OBSERVATION: |  |
| Background Chemical behaviour plays an important role in determining the consequences of postulated accident scenarios for a nuclear facility. It can influence the progression of an accident by determining the phases of materials, their physical and chemical properties, and heat transfer processes. It also influences the distribution, release and retention of fission products, and thus the potential source term and radiological consequences of an accident. This is true for both design basis and severe accidents, although for the latter the uncertainties are often larger. Chemical behaviour is also important in determining the generation, transport and removal of combustible gases that could be generated during faults, particularly during severe accidents. This aspect is already considered as part of RO-RRSMR-009 (Ref. [1]), and therefore is not part of this Regulatory Observation (RO) or considered further below. In safety cases it is common to make assumptions and simplifications about the chemical behaviour that may take place during accidents as part of determining the potential consequences. Given the direct impact that these assumptions and simplifications can have on the results of the consequence analysis, ONR expects adequate justification that chemistry behaviour are applicable to the specific facility design and are representative of the postulated accident sequences considered. During Step 2 of the Generic Design Assessment (GDA) of the Rolls-Royce SMR design, the Requesting Party (RP), Rolls-Royce SMR Ltd, submitted its strategy and intentions for the development of the severe accident chemistry aspects of its Environment, Safety, Security and Safeguards (E3S) case (Ref. [2]). In Step 3 of GDA a document setting out the RP’s intentions for scope and deliverables in the chemistry topic area was issued (Ref. [3]), describing the intent to submit a first issue of “Severe Accident Chemistry Analysis Report” in June 2025. In place of that submission, an alternative submission was delivered (Ref. [4]). ONR has reviewed Ref. [4] and its underlying references (Refs. [5], [6] and [7]) and, whilst some relevant information is presented, ONR has identified that further work is required by the RP to document and justify that its approach to chemical behaviour is adequate. Ref. [4] focusses at a high level on the treatment of chemical behaviour in the analysis of radiological consequences in severe accidents; little detail is provided on the methods to be used, why they are appropriate, and on the supporting evidence that is planned to be produced. Additionally, no information is provided in Ref. [4] on how chemical behaviour in the progression of severe accidents is being considered and assumptions appropriately justified, or alternatively, how a case will be made that such chemical effects are not important in severe accidents in the Rolls-Royce SMR. The submission and underlying references lack a consistent narrative and specificity to the Rolls-Royce SMR design. The first issue of “Severe Accident Analysis Report” was not submitted in June and has been delayed to December 2025. Based on ONR’s review of Ref. [4], ONR has limited confidence that an adequate demonstration that appropriate assumptions have been made on the influence of chemistry in severe accidents will be provided, that is suitably representative of the generic Rolls-Royce SMR design. Relevant Legislation, Standards and Guidance The ONR Safety Assessment Principals (SAPs) (Ref. [8]) of most relevance to this RO are: - ECH.1 Safety cases should address all chemistry effects important to safety. The safety case should demonstrate that a comprehensive and systematic analysis has been performed to identify and analyse how chemistry can impact safety during accident conditions. - FA.15 Fault states, scenarios and sequences beyond the design basis that have the potential to lead to a severe accident should be analysed. The severe accident analysis should be based on an adequate understanding of the severe accident phenomena and accident progression. Where severe accident uncertainties are judged to have a significant effect on the assessed risk, research aimed at confirming the modelling assumptions should be performed. - AV.2 Calculation methods used for analyses should adequately represent the physical and chemical processes taking place. The physical and chemical form of radioactivity need to be considered, but also the physical and chemical processes assumed to be taking place, need to be representative. - AV.3 The data used in the analysis of aspects of plant performance with safety significance should be shown to be valid for the circumstances by reference to established physical data, experiment or other appropriate means. - AV.6 Studies should be carried out to determine the sensitivity of the analysis (and the conclusions drawn from it) to the assumptions made, the data used and the methods of calculation. ONR’s Technical Assessment Guide (TAG) for chemistry assessment (Ref. [9]) also provides relevant guidance, including that: - The chemical and physical form of radioactivity plays an important role in determining the relevant phenomena which govern its long-term post-accident behaviour. - There should be adequate justification that chemistry phenomena are applicable to the specific facility design and are representative of postulated accident sequences. - The performance of any claimed safety systems to remove and retain radionuclides, the assumed chemical and physical forms of radionuclides, and how these might evolve over the course of an accident are key considerations. ONR’s GDA technical guidance (Ref. [10]) notes that the chemistry assessment also considers the effects of chemistry during fault conditions, as this can influence the rate of progression and ultimate consequences of a particular fault. This includes the generation, transport and behaviour of radionuclides and reactive species and in particular, will focus on the adequacy of any assumptions or treatment in supporting analysis. This will span the full range of fault conditions from Design Basis faults up to and including Severe Accidents. A range of international guidance is also of relevance, including: - IAEA SSG-2 (Ref. [11]) paragraph 2.17: Under accident conditions, source term evaluation requires simulation codes capable of predicting fission product release from fuel elements, transport through the primary system and containment or spent fuel pool building, the related chemistry affecting this transport and the form in which the radioactive material would be released. - IAEA SSG-4 (Ref. [12]): - Paragraph 6.11 notes that interactions between various physicochemical processes should be correctly addressed in the code selected to perform the analysis of the progression of severe accidents. - Paragraph 10.17 notes that in the source term analysis, all of the processes that affect the release and transport of radioactive material inside the containment and in adjacent buildings should be modelled. These processes include retention of radioactive material inside the containment and adjacent buildings; resuspension, re-vaporisation, condensation and re-entrainment (e.g. as a result of energetic phenomena, chemical reactions or mechanical effects). Regulatory Expectations In line with the standards and guidance described above, ONR expects a severe accident chemistry safety case for a new reactor to demonstrate: - Adequate representation of all the chemistry processes that influence the progression of the severe accident and the eventual release of radioactivity; - Use of appropriate and validated methods; - Appreciation of the uncertainties in the models and the potential effect on the results of the analysis, including demonstration that there are no cliff-edge effects. The purpose of this RO is for the RP to define how it intends to deliver a clear and consistent E3S case narrative, demonstrating appropriate consideration of chemical behaviour in the progression of severe accidents and in severe accident radiological consequences for the Rolls-Royce SMR design. The information provided in response to this RO should give details of the bounding analysis being undertaken, the inputs to the analyses and why they are appropriate, and the version of the Rolls-Royce SMR design reference the analysis will represent. The information should be demonstrably specific to the Rolls-Royce SMR design and should make clear how the consideration of chemical effects in severe accident scenarios supports other parts of the E3S case. While iodine chemistry may be a key aspect, since the properties of iodine mean that it is particularly important in estimating radiological consequences, the response should be wider than this. ONR expects similar considerations relevant to combustible gases during severe accidents to be provided as part of the overall Rolls-Royce SMR E3S case, however we consider this aspect to be part of RO-RRSMR-009. References [1] RO-RRSMR-009 Safety Case for Hydrogen Management in Severe Accidents, Revision 1, June 2025, (Record ref. ONRW-2019369590-7299) [2] Rolls-Royce SMR Accident Chemistry Strategy Report, SMR0008800, Issue 2, April 2014, (Record ref. ONRW-2019369590-8765) [3] Rolls-Royce SMR Generic E3S Case Scope and Deliverable Document – Chemistry, SMR0011037, Issue 3, June 2025, (Record ref. ONRW-2019369590-22046) [4] Rolls-Royce SMR Overview of Accident Chemistry Support to Radiological Consequences Analysis of Severe Accidents, SMR0024657, Issue 1, June 2025, (Record ref. ONRW-2019369590-22142) [5] Rolls-Royce SMR Severe Accident Off-site Consequences Methodology, SMR0007629, Issue 2, September 2024, (Record ref. ONRW-2019369590-16943) [6] Rolls-Royce SMR Severe Accident Analysis Summary Report, SMR0006219, Issue 2, January 2025, (Record ref. ONRW-2019369590-16941) [7] Rolls-Royce SMR Severe Accident RCA Summary Report, SMR0021246, Issue 2, April 2025, (Record ref. ONRW-2019369590-20235) [8] Office for Nuclear Regulation Safety Assessment Principles for Nuclear Facilities 2014 Edition, Revision 1, January 2020. www.onr.org.uk/media/pobf24xm/saps2014.pdf [9] Office for Nuclear Regulation Technical Assessment Guide NS-TAST-GD-089 Chemistry Assessment, Issue 1.1, December 2022. www.onr.org.uk/publications/regulatory-guidance/regulatory-assessment-and-permissioning/technical-assessment-guides-tags/nuclear-safety-tags/ns-tast-gd-089 [10] Office for Nuclear Regulation New Nuclear Power Plants: Generic Design Assessment Technical Guidance, ONR-GDA-GD-007 Revision 0, May 2019. www.onr.org.uk/media/c2delysl/onr-gda-gd-007.docx [11] IAEA Deterministic Safety Analysis for Nuclear Power Plants, Specific Safety Guide No. SSG-2, Revision 1, 2019. www.iaea.org [12] IAEA Development and Application of Level 2 Probabilistic Safety Assessment for Nuclear Power Plants, Specific Safety Guide No. SSG-4, Revision 1, 2025. www.iaea.org |  |
| REGULATORY OBSERVATION ACTIONS |  |
| RO-RRSMR-013.A1 – Define the scope of the consideration that will be given to chemical behaviour during severe accidents and how it will support the E3S case In response to this Regulatory Observation Action, Rolls-Royce SMR should: - Provide documentation which describes the detailed scope of “Severe Accident Chemistry Analysis Report” Issue 1, including details of any exclusions from the scope. - Provide an outline structure of the report indicating the main sub-sections. - Provide a plan of the work that is scheduled to feed in to the report and in to other relevant submissions. - Describe where “Severe Accident Chemistry Analysis Report” Issue 1 sits within the E3S case structure. - Describe how the analysis defined in action 2 supports the E3S case, including: - The relevant claims and arguments the analysis will support; - How the conclusions of the work will be presented in E3S chapter 20 and underlying documentation; - How the consideration of chemical effects in severe accident scenarios supports other parts of the E3S case. Resolution required by 'to be determined by Rolls-Royce SMR Resolution Plan' |  |
| RO-RRSMR-013.A2 – Define the bounding analysis to be undertaken In response to this Regulatory Observation Action, Rolls-Royce SMR should: - Provide documentation that describes how uncertainties associated with chemistry effects in severe accidents will be bounded by the analysis assumptions / methods selected. - Describe what the key inputs are to the analysis and why they are appropriate. - Describe how the chemistry effects, that are important in determining the progression of the accident and in the analysis of radiological accident source terms, will be identified and justified. - Provide documentation that explains which version of the Rolls-Royce SMR design reference point the analysis will represent. - If this is different to the final design reference point in GDA, provide a summary of how uncertainties in the design will be bounded. Resolution required by 'to be determined by Rolls-Royce SMR Resolution Plan' |  |

| REQUESTING PARTY TO COMPLETE |  |
| --- | --- |
| Actual Acknowledgement date (dd/mm/yy): |  |
| RP stated Resolution Plan agreement date (dd/mm/yy): |  |