ONR Technical Assessment Guide Emergency Power Generation

Contents

1.	Introduction	3

2.	Purpose and scope	4

3.	Relationship to licence and other relevant legislation	5

4.	Relationship to Safety Assessment Principles, WENRA Reference Levels, and IAEA Safety Standards and Guides	7

5.	Advice to inspectors	9

Appendix 1 – Guidance for undertaking mechanical engineering inspections of EPGSs	23

Appendix 2 – Guidance on the use of biodiesel	28

References	29

Glossary	30

List of key acronyms, initialisms and abbreviations	31

Document control information	32

# Introduction

This Technical Assessment Guide (TAG) is part of a suite of guidance available to ONR inspectors to assist in their application of the Safey Assessment Principles (SAPs) [1] which are used in the technical assessment of the safety cases for nuclear facilities and in the formation of regulatory judgements.

This TAG has been written with due regard for relevant legislation, licence conditions and international guidance. The overarching relationships between the TAGs and these areas of legislation and guidance are discussed further in “An Introduction to ONR's technical assessment and inspection guides” [2].

# Purpose and scope

This TAG guides ONR inspectors assessing Emergency Power Generation systems (EPGS). An EPGS comprises the prime mover, generator, and auxiliaries up to the generator terminals, and the electrical equipment that enables connection of generator(s) to the plant and its structures, systems, and components (SSCs).

Following loss of normal power (for example, Loss of Off-Site Power (LOOP)), an EPGS supplies electrical power to the nuclear safety systems identified in the licensee’s safety case, typically to maintain essential cooling and containment.

The guidance also applies to mobile generators; inspectors should consider the adequacy of transport, connection, and re-fuelling provisions.

This TAG focuses on mechanical engineering. Further guidance is in Appendix 1 and following sections:

## Electrical systems

Inspectors are advised to consider the guidance within the Essential Services TAG [3] in carrying out the assessment of EPGSs.

## Control and instrumentation systems.

The control and instrumentation (C&I) systems, including elements such as the starting system, automatic voltage regulator, EPGS synchronising schemes and multi-set controllers, are key considerations when assessing the overall ability of the EPGS to meet the safety case claims.

If these systems contain software elements (as in the case of smart devices, for example), ONR’s expectations are as set out in SAP ESS.27 and further developed in the TAG on computer-based safety systems [4].

Other C&I issues that should be considered but are not included within the scope of the TAG are:

Potential for environment, human error or cyber security threat to prevent correct operation.

Support and auxiliary systems commensurate with claims being made (eg power supplies and HVAC).

Diagnostics to identify faults and appropriate measures to address faults (eg critical spares holding and availability of technical support).

# Relationship to licence and other relevant legislation

## Licence Conditions

The following LCs are particularly relevant to EPGS; however, the list is not exhaustive:

Licence Condition 10: Training

Licence Condition 11: Emergency Arrangements

Licence Condition 12: Duly authorised and other suitably qualified and experienced persons

Licence Condition 15: Periodic review

Licence Condition 20: Modification to design of plant under construction

Licence Condition 21: Commissioning

Licence Condition 22: Modification or experiment on existing plant

Licence Condition 23: Operating Rules

Licence Condition 24: Operating instructions

Licence Condition 25: Operational Records

Licence Condition 26: Control and supervision of operations

Licence Condition 27: Safety mechanisms, devices and circuits

Licence Condition 28: Examination, inspection, maintenance and testing

Several statutory instruments relate to management of EPGS. 
These include:

Health and Safety at Work Act (HSWA) 1974

The Supply of Machinery (Safety) Regulations 2008

The Provision and Use of Work Equipment Regulations 1998

The Management of Health and Safety at Work Regulations 1999

The Electromagnetic Compatibility Regulations 2016

The Low Voltage Electrical Equipment (Safety) Regulations 1989

The Electricity at Work Regulations 1989

The following Statutory Instruments may also be applicable (for example, compressed air systems for emergency generator starting):

The Pressure Systems Safety Regulations 2000

The Pressure Equipment (Safety) Regulations 2016

The Control of Substances Hazardous to Health Regulations 2002

# Relationship to Safety Assessment Principles, WENRA Reference Levels, and IAEA Safety Standards and Guides

## Safety Assessment Principles

Whilst the SAPs [1] do not specifically mention EPGSs, ONR inspectors should take the following into consideration in their assessment:

ECS.1 to ECS.5 (Safety categorisation and safety classification)

EQU.1 (Equipment qualification)

EDR.1 to EDR.4 (Design for reliability)

ERL.1 to ERL.4 (Reliability claims)

ECM.1 (Commissioning)

EMT.1 to EMT.8 (Maintenance, inspection and testing)

EAD.1 to EAD.5 (Ageing and degradation)

ELO.1, 2 and 4 (Layout)

EHA.1 to EHA.17 (External and internal hazards)

ESS.1 to ESS.27 (Safety systems)

ESR.1 to ESR.7 and ESR.9 to 10 (Control and instrumentation of safety-related systems)

EES.1 – EES.9 (Essential services)

EHF.1 to EHF.10 (Human factors)

## WENRA

This TAG considers guidance given in the WENRA Safety Reference Levels for Existing Reactors 2020 [5]. The following areas are relevant to EPGSs:

Issue E: 	Design Basis Envelope for Existing Reactors

Issue F: 	Design Extension of Existing Reactors

Issue I: 	Ageing Management

Issue K: 	Maintenance, In-Service Inspection and Functional 
			Testing

Issue LM: 	Emergency Operating Procedures and Severe Accident
			Management

Issue R: 	On Site Emergency Preparedness

Issue T: 	Natural Hazards

## IAEA

IAEA Safety Standard for the safety of nuclear power plants (NPPs) design 
(SSR-2/1, Requirement 68) [6], requires the emergency power supply at the nuclear power plant shall be capable of supplying the necessary power in anticipated operational occurrences and accident conditions, in the event of the loss of off-site power.

IAEA Specific Safety Guide on the design of electrical power systems for nuclear power plants (SSG-34) [7] , provides recommendations on the provision of standby and alternate AC power sources. ONR considers SSG‑34 to represent relevant good practice when assessing EPGS. Although developed for NPPs, ONR judges the guidance to be applicable to non‑NPP situations.

# Advice to inspectors

## Overview

This guide sets out what ONR considers relevant good practice (RGP) taken from national and international guidance. In support of this TAG, ONR commissioned a report [8] to identify national and international RGP for diesel generators.

A multi-discipline approach should be taken for the assessment of EPGSs, this will typically require interaction between the following specialisms:

Mechanical engineering

Electrical, Control and Instrumentation engineering

Fault studies

Internal hazards

External hazards

Human factors

## Emergency power generation system (EPGS) description

An EPGS (diesel or gas turbine and generator) supplies essential nuclear safety loads when normal power is lost. An EPGS comprises primary SSCs (deliver power) and ancillary SSCs (infrastructure / services). Examples are as presented in Table 1.

The safety case should demonstrate that the EPGS has adequate energy (for example, electricity and compressed air) stored for engine starting and restarting.

Table 1 - Examples of EPGS - Primary and ancillary SSCs.

| Primary SSC | Ancillary SSC |
| --- | --- |
| Diesel engine or gas turbine Electrical generator Generator exciter Filtered combustion air intake. Cooling system (see below) Lubrication system Fuel tank and delivery system. Starter system (for example, compressed air and batteries) Electrical protection system for the EPGS Control and instrumentation system. Distribution and connection of power to plant | Building structure and enclosure Foundations Exhaust extract system. Heating and ventilation system Filling and draining equipment. Maintenance equipment (ego lifting and handling) |

## Safety case requirements

It is expected that the safety case should:

Establish the safety functional requirements (i.e., claims) for the EPGS.

Determine the safety classification of the EPGS (based on the relevant safety classification of the SSC(s) they support).

Demonstrate that the EPGS is meeting the relevant claims and safety classification (through a combination of design considerations, commissioning, testing and EIM&T).

For the purposes of this guide, the term ‘mission time’ is the time an EPGS is required to provide back-up power as defined by the safety case.

When determining the safety function requirements, it is essential to determine:

The electrical generation capacity required;

The time over which the generation is required;

What start-up time is acceptable (i.e., delay) before the generation is effective;

The appropriate safety function category (SAP ECS.1 (Safety categorisation));

The appropriate safety classification of the SSCs that make up the EPGS in its role as an essential support system (SAP ECS.2 (Safety classification of structures, systems and components));

Internal and external hazards (SAP EHA.1 to 19);

The interfaces and supporting systems needed to ensure successful delivery of the electrical generation to the specified safety-related electrical loads.

It should be noted that some of the safety measures at each defence in depth level may be diverse systems and, hence, do not place any claims on the EPGS. If such measures offer an adequate means of protection, this might provide adequate diversity eliminating the potential for common cause failures associated with diesel generator (DG) and gas turbine generator (GTG) systems.

Adequate defence-in-depth provision relies on:

There being sufficiently robust measures at each level;

Common cause failures should not adversely affect levels of redundancy and diversity (SAP EDR.3 (Common cause failure)).

A fault studies specialist may need to assess the licensee’s safety case and EPGS claims. Clarification is required on whether EPGS support applies to design basis fault scenarios (Levels 1–3 of defence in depth) or beyond design basis scenarios (Levels 4–5). This affects EPGS safety classification and ONR’s expectations for substantiation detail and rigour.

The operating and EIM&T strategy should prioritise the ability to provide reliable emergency power generation. It is not expected that EPGSs should operate routinely for commercial gain (for example, revenue or reduce operating costs), as this may deplete fuel stocks and shorten LOOP supply duration. Extended non-safety operation may also increase wear and reduce reliability. Where the safety case requires extended operation for testing 
(for example, performance demonstration or fuel refresh), a reasonable side benefit might be commercial gain. Such practices would also have be agreed with the Environment Agency (EA) and Scottish Environment Protection Agency (SEPA).

- Note: An EPGS may be combustion plant and require a permit from the EA. If the total thermal input exceeds 20 MWth [thermal megawatts], the combustion plant is also a 'regulated activity' as defined in the Greenhouse Gas Emissions Trading Scheme Regulations (2012) and will require a permit under those regulations.

Inspectors should confirm the licensee has considered how generation capability will be used during an extended power loss. Emergency power may be needed beyond the design basis mission time. Demand for some essential services may decrease over time (for example, decay heat removal), allowing fuel conservation. A risk-based approach should prioritise fuel use, as illustrated in Figure 1.

Figure 1 - Extended power loss scenario

In line with SAP SC.6 [1], the safety case should identify key operational and management aspects for maintaining safety and how these will be implemented. This includes:

The operating limits and conditions (operating rules) required (LC23);

The procedures and instructions required (LC24);

The necessary safety mechanisms, devices and circuits (SMDCs) installed and functioning (LC27);

The examination, inspection, maintenance and testing regimes justified in or assumed by the safety case (LC28);

Control, supervision, qualification and training and other safety management requirements (LC10 and LC12);

Inputs to emergency arrangements (LC11).

Inspectors should review how licensees monitor and demonstrate EPGS performance against safety case claims, including reliability.

Safety case claims should not be compromised by dependencies on supporting services. For example, EPGSs should not only store sufficient energy for engine starting and restarting but have a suitable means to replenish the lost energy.

Licensees should be able to demonstrate from a suitable test programme that there are sufficient fuel and services capacity (for example, batteries and compressed air) to meet the safety case demand.

### System management and accountabilities

Reliability claims within safety cases should address the risk and evaluate the consequences of EPGS ‘failure to start’ and ‘failure to continue running’ to operate for a defined time.

It is therefore expected that licensees will gather and analyse failure and asset condition data for the purpose of providing confidence, identifying shortfalls and, hence, suitable improvement. The licensee should therefore have clearly defined safety case derived criteria against which such technical assessments can be made. This will include a clear definition of the actions that need to be taken to secure safety of the plant or facility.

For new EPGS plant, safety case requirements should be determined early. As a means of identifying safety improvements and increasing plant availability, the original equipment manufacturer (OEM) and maintenance and operational staff should be actively involved in the design process.

## Learning from the Fukushima accident

In March 2011, a seismic event triggered a tsunami that overwhelmed seawalls and flooded the Fukushima Daiichi NPP, destroying seafront structures and five of six emergency diesel generators due to inadequate flood protection.

Inspectors should expect licensees to show learning from the Fukushima accident [9] in new EPGS facilities, incorporating suitable and sufficient redundancy, diversity, segregation, and layout. The TAG on redundancy, diversity, segregation and layout of mechanical plant should be considered in these assessments [10].

Periodic Reviews (LC15) of existing facilities should also reflect Fukushima lessons. Licensees are expected to consider new technologies and global operating experience to improve EPGS resilience.

## Redundancy

The safety case should specify the number of EPGs within an EPGS to meet deterministic and probabilistic safety requirements, including redundancy to maintain the safety function if one or more EPGs are unavailable 
(for example, failure or planned EIM&T).

Support equipment (for example, cooling and lubrication pumps) for each EPGS should draw power from its own division, not a common source, to preserve redundancy and independence.

Sufficient EPGSs must always be available to meet emergency power needs, as defined by the safety case (LC23 – Operating Rules and LC24 – Operating Instructions) to limit risk from plant unavailability.

Maintenance, test, and repair impacts on EPGS reliability should be assessed. If reliability falls below safety case claims, the nuclear plant it serves should be placed in a safe state and the out-of-service EPG substituted or restored within a specified time.

## Segregation

System segregation reduces common cause failure risk by separating components with distance or physical barriers. The safety case should show EPGSs and key components (for example, fuel tanks, feed lines) are adequately segregated.

Evidence should confirm functionality under relevant internal hazards 
(for example, projectiles, fire, internal flooding) and external hazards 
(for example, aircraft crash, flooding, seismic activity) (SAP EHA.6 (Analysis) [1]).

## Layout

EPGSs should remain operable and accessible during design basis faults, accidents, or hazards, especially where safety-related SSCs are co-located with non-safety plant (SAP ELO.1 (Access) [1]).

Manufacturer layouts may reflect non-nuclear requirements and be unsuitable for nuclear use. Alternative layouts should ensure EPGSs perform their safety function after any initiating event.

Layouts must provide local access for manual intervention where needed. Design, construction and installation should align with safety case claims on access during operation and fault conditions, for example, refilling fuel tanks after a seismic event.

## Diversity

Engineering diversity means using dissimilar methods to achieve the same safety function, for example, differing physical features or equipment from different manufacturers. The safety case should show diversity has been achieved as far as reasonably practicable (SAP EDR.2 (Redundancy, diversity, and segregation) [1]).

Key EPGS elements such as DGs and GTGs often use ‘Commercial Off The Shelf’ (COTS) equipment from a small number of specialised manufacturers. Diversity options should be explored, but changes to proven designs or supply chains may reduce reliability and durability.

Diversity may be claimed by sourcing generators from different manufacturers or types with varied configurations and parameters. 
However, units may share common components (for example, castings, bearings, injectors, controllers), making true diversity impracticable.

Diversity may also involve providing both DG and GTG systems, though these can share components and sub-systems (for example, starter air compressors and generator sets).

Cooling system choice offers diversity: diesel engines may be water or air-cooled; gas turbines are air-cooled. Each system is vulnerable to component failures (for example, pumps, fans). Diversity should extend to component level to avoid failure modes affecting all generators. Licensees should demonstrate cooling system reliability and fault tolerance do not compromise nuclear safety function.

## Dependent failures

Inspectors should confirm the risk from dependent EPGS failures is reduced to an acceptable level within safety case limits, considering deterministic and probabilistic aspects.

Multiple failures may arise from shared weaknesses or dependencies, even in dissimilar generators from different subdivisions of one company. Systematic failures increase with complexity.

Such failures can disable all redundant components in one protection system or across systems, reducing reliability beyond that expected from random failures alone. Refer to [10] for guidance.

ONR inspectors should review the measures taken by the licensee to limit the effect of dependent failures on EPGSs.

Where multiple generation sets are used, the safety case should define redundancy, diversity, and independence to minimise common cause failures (CCF). Refer to SAP EDR.2 and EDR.3 [1].

## Start up

Starting an EPGS is critical to its safety function. It must generate sufficient power within the time specified by the safety case. Licensees should show starting system reliability matches overall reliability claims.

Common to all turbines, GTGs will only work when the fuel is ignited and the blades are spinning at sufficient speed to compress the incoming air to the required pressure. An additional method is needed to spin the compressor up to speed, which affects starting time and EPGS selection.

Starter systems should have adequate services (for example, battery capacity, compressed air) and fuel for multiple start attempts and continued operation beyond normal start-up. This should be factored into the capacity of the starter system.

Guidance on DGs within this TAG applies to diesel engines used for starting GTGs.

### Spurious operation

EPGSs may face spurious operation faults as well as failures. Licensees must ensure measures prevent adverse effects from spurious operation or other system failures, including hidden dependencies (SAP ESS.17, [1]).

## External hazards

External hazards challenge EPGS delivery of the safety function. The safety case may require operation during and after such events. Inspectors should consider the TAG on external hazards [11].

### Design basis events

Design should account for power derating at high ambient temperatures.

Combustion air intakes may need frost protection at low temperatures; Control and instrumentation may also be affected (for example, fuel level gauges on external tanks).

### Loss of normal power source

Loss of offsite power may range from millisecond dips to multiday blackouts. Onsite infrastructure failures, maloperation, and grid faults (phase unbalance, high / low voltage, high / low frequency) may require EPGSs as the alternative source.

### Aircraft crash

The safety case should define EPGS facility withstand requirements for design basis aircraft crash, including fire and explosion. Where no withstand is required, segregation and redundancy should ensure the loss of one (or more) EPGSs is acceptable.

### Earthquake / seismic event

EPGSs are likely to be required after seismic events causing loss of supply, sub-station trip, or reactor shutdown. EPGSs should be seismically assessed to meet safety case requirements.

Supporting structures should also withstand the design basis earthquake and limit component movement (for example, couplings, fuel lines) to maintain functionality.

### Flooding

EPGSs should be located above the level of the design basis flood. 
Where this is not practicable, permanent external barriers such as levees, sea walls and bulkheads should be provided.

For existing facilities where this is not practicable, suitable permanent or temporary protections may be used (for example, “drop-in” barriers, drains, sumps, pumps). Arrange electrical switchboards and equipment to avoid flooding effects. Inspectors should confirm arrangements to deploy temporary measures in time, with the minimum trained staff stated in the safety case and evidence of regular deployment trials.in barriers, drains, sumps, pumps). Arrange electrical switchboards and equipment to avoid flooding effects. Inspectors should confirm arrangements to deploy temporary measures in time, with the minimum trained staff stated in the safety case and evidence of regular deployment trials.

Licensees should maintain an EIM&T programme to ensure temporary flood protection is stored securely, in satisfactory condition and working order.

Where practical, site EPGSs sufficiently above ground level to reduce rainwater ingress; size storm drains for design basis rainfall.

### Internal hazards

Protect EPGS facilities (for example, by location or barriers) from other plant, equipment or materials that could generate hazards (for example, fire, projectiles).

### Fire

Suitable and sufficient fire protection shall be provided within the facility. Specialist advice may be sought from an Internal Hazards or Fire Inspector, as this may exceed normal fire detection and protection measures. 
Minimise fuel and lubrication leaks through adequate EIM&T and housekeeping to detect and address leaks before accumulation.

### Lifting equipment

Permanently installed cranes and hoists are expected for maintenance. Lifting equipment should be positioned or restrained to avoid impacting ‘in service’ EPGSs, specific consideration should include earthquake withstand of the crane / hoist.

## Commissioning

Commissioning trials should demonstrate confidence that emergency generators and ancillary equipment meet the declared safety function, including load for the mission time in the safety case (SAP ECM.1 (Commissioning) [1]).

Beyond individual sub-system tests, the plan should include a full system test to exercise common equipment (for example, fuel, oil, cooling, control cabinets, batteries) and reveal weaknesses under sustained demand.

## Examination, inspection, maintenance, and testing

Safety classification of SSCs, based on fault analysis, is essential for forming a suitable EIM&T regime. All EPG SSCs should be designed, installed, commissioned, operated, and maintained to a quality level matching their classification (SAPs ECS.1–ECS.5 [1]).

Safety management often divides the EPGS into sub-systems with EIM&T applied to each to optimise performance.

Licensees should demonstrate confidence that EPGSs meet declared reliability and safety functions, including load for the mission time (SAP EMT.6 [1]).

EPGSs must always deliver their design intent through an effective EIM&T programme. Reliability should be proven by testing and availability monitored by a suitable regime.

The adequacy of EPGS availability might be affected by EIM&T requirements. The inspector should establish that the licensee’s operating rules and operating instructions specify suitable and sufficient levels of EPGS redundancy, diversity, and segregation for safe nuclear plant operation. The actions to be taken (for example, safe plant / reactor shutdown) in response to partial or total loss of EPGS availability should be clearly stated.

Electrical generators are specialist equipment, and it is therefore expected that licensees will have significant reliance on original equipment manufacturers (OEM) for EIM&T, technical support and advice. For example, routine EIM&T activities may be undertaken by the licensee’s maintenance personnel, but major overhauls and breakdowns are often carried out by OEM service organisations. Inspectors should seek evidence that all EIM&T is carried out by suitably qualified and experienced personnel (SQEP).

Electrical generators require regular preventative maintenance and testing. Run tests assure readiness and may also serve a maintenance function 
(for example, lubrication). Tests should follow the plant schedule and involve OEM consultation for operating experience feedback (SAP EMT.7 [1]).

### Testing

There have been several reports which present an analysis of failures of emergency DGs which can also apply to GTGs [8]. The reports give a breakdown of failures within the sample. The top five categories are listed in Table 2.

Table 2 - EPGs failures

| Failure to start | Failure to run |
| --- | --- |
| - control and instrumentation system. - starting sub-system - electrical generator - diesel engine - lubrication oil | - engine - cooling system - fuel oil - generator - control and instrumentation system |

About two thirds of failures were found through testing, underscoring the need for a suitable and sufficient test programme. Representative example:

“Both emergency DGs failed to continue running 22 hours into 24-hour test due to a short on voltage suppression devices due to inadequate cooling in the excitation cabinet.”

A successful test would be both generators running for 24 hours. This was a CCF because shared excitation equipment was inadequately cooled; testing units one at a time might have missed it.

Regular EPGS testing should demonstrate availability, reliability, and capability per the safety case (SAP EMT.7 (Functional testing) [1]).

So far as is reasonably practicable, tests should be full system tests from engine to loads to avoid overlooking subsystems. Conduct tests in islanded mode to demonstrate speed / voltage control and, where applicable, load shedding and sequencer operation.

Where full system tests are not practical, or where appropriate in between full system tests, testing of sub-systems should be undertaken. Such testing may be required to demonstrate the capability of those systems in response to specific events. Examples, of this could include demonstrating manual operation of the EPGS, or demonstrating the full power rating of the EPGS, which may only be possible in normal conditions through parallel operation with the offsite power supply or operation with a load bank. It is expected that licensees can demonstrate that such testing regimes encompass all required conditions of the safety case and do not exclude any required sub-systems (SAP EMT.6 (Reliability claims) [1]).

The licensee should demonstrate that it has adequately considered a range of factors and evaluated the impact of alternative options to arrive at a reasonably practicable testing regime.

Maintenance induced defects are a common failure mechanism and, where maintenance of similar equipment is undertaken in short succession, it can lead to common cause failure of redundant and diverse equipment. It is expected that testing should be undertaken following completion of maintenance activities to demonstrate that the equipment can deliver its safety case requirements. The licensee’s EIM&T programme should also ensure that the fuel is stored safely and securely and is maintained in a satisfactory condition for reliable operation.

Periodically test and condition monitor the fuel oil system per the plant maintenance schedule, followed by visual examination for leaks, structural distress, or corrosion (SAP EMT.5 (Procedures) [1]).

### Spares

The management of spares holding is an important area that can impact on the safety case claims. Licensees should define spares policy and critical holdings considering obsolescence, failure rates, repair time, lead time, and OEM support (SAP EAD.5 (Obsolescence) [1]).

## Equipment outages

Sufficient EPGSs must always be available to meet emergency power needs, as defined by the safety case (for example, Operating Rules and Instructions) to limit risk from plant unavailability.

The impact of the anticipated maintenance, test, and repair work on the reliability of EPGSs should be considered. If the resultant reliability or availability to perform a safety function is such that the EPGS no longer meets the criteria used for design and operation, the nuclear plant it serves should be placed in a safe state and the EPGS temporarily out of service should be substituted or restored within a specified time.

## Fuel management

The safety case should state the mission time for EPGSs following LOOP events and the minimum fuel stocks in Operating Rules / Instructions. Operational records should confirm minimum levels (SAP FA.8 (Linking of initiating faults, fault sequences, and safety measures) [1]).

Minimum fuel stocks should be stated in the safety case and be sufficient to allow for periodic maintenance/test running of the EPGSs. Licensees should have effective arrangements to replenish tanks in time to maintain minimum levels.

### Fuel specification and quality

Licensees should specify the required fuel quality and apply controls to ensure supplier fuel meets the standard.

Within the EU, diesel for road ranges from 7% (B7) to 10% (B10). Eventually, biodiesel might be introduced for all applications. It is therefore possible that biodiesel might inadvertently or otherwise enter EPG diesel systems.

Biodiesel can adversely affect diesel engine performance. Inspectors should seek assurance that licensees recognise these risks and are taking appropriate action. Refer to Appendix 2 for guidance.

Licensees should have a programme in place to ensure the initial and continuing quality of the fuel oil by regular sampling and, if appropriate, physical property testing.

Fuel tank location is normally set by the DG / GTG manufacturer; consider alternative positions that improve resilience to fault conditions without compromising the primary safety function.

The tanks should be protected against external and internal corrosion. 
Tanks should be checked for water content and any accumulated condensate removed on a regular basis.

Periodically remove stored fuel to clear sediment and clean tanks using methods that do not degrade fuel quality. For example, cleaning fluids should not introduce surfactants into the fuel system.

Cleaning may coincide with pressure testing and visual examination of the tanks for evidence of component leakages, structural distress, or corrosion.

Fuel quality is affected by temperature. At low temperature, wax comes out of solution in diesel fuel, and it becomes gel-like. If this happens, the diesel will not readily flow through valves and other devices. Temperatures should be controlled to ensure that the EPG fuel is always maintained in a satisfactory condition.

## Asset management

Facility life may exceed EPGS life or OEM support period. Licensees should have a strategy for ageing and obsolescence, which may include replacing EPG systems. Replacement should not compromise the EPG safety function (SAP EAD.5 (Obsolescence) [1]).

# Appendix 1 – Guidance for undertaking mechanical engineering inspections of EPGSs

- EPGs are specialist COTS equipment. ONR inspectors should therefore not attempt to influence the established principles of the OEM design or how the EPG is intended to function. The focus for the mechanical engineering assessment of EPG systems is most likely to be the suitability of the EPG system layout and the adequacy of the EIM&T provisions to ensure reliable operation on demand.

International operating experience identifies nine common EPG failure causes, seven linked to inadequate EIM&T. Mechanical engineering issues are presented in Table 3.

## EIM&T

The licensee’s maintenance procedures should be inspected to ensure that relevant good practice is adhered to, and equipment is maintained in accordance with the OEM’s recommendations. Typical examples are as follows:

Maintenance, periodic inspections and testing should be in accordance with the OEM’s instructions subject to oversight from the licensee as intelligent customer.

Adequate lubrication should be established before all planned starts (including maintenance running). For DGs, this would typically involve starting the engine at low speed and running for a set period to deliver lubrication to all DG components. Running speed and load should be increased and decreased gradually.

Bearing inspections should be carried out at suitable intervals.

Regular oil sampling and analysis, for example, for metal content and degradation

Regular replacement of oil and air filters and inspection of oil strainers. This provides an opportunity for analysis of the oil filter media and any deposits found.

Verification of fuel to ensure continued acceptability for emergency use, including low temperature suitability, i.e. the abnormal low temperature conditions stated in the nuclear safety case.

Effects of ageing, for example, degradation of rubber components.

Appropriate use of condition monitoring and trending to identify adverse or deteriorating performance across all EPGSs.

Evidence of learning from internal and external operating experience to improve maintenance regime and practices.

Good housekeeping practices, for example, exclusion of foreign materials and contaminants.

Inspectors should be aware that severe ageing can result from factors such as starting too often, sustained low or high engine loading and rapid engine loading.

Table 3 - Common mechanical failures

| Issue | Design | Site inspection |
| --- | --- | --- |
| Low coolant level | EPG coolant systems should be provided with a means of inspecting the coolant levels to ensure that they are within the acceptable range specified by the OEM. | Evidence of regular inspection of the coolant levels should be recorded in the maintenance logs, together with any actions taken by the licensee to address low coolant levels. |
| Leaks (fuel, oil, or coolant) | Diesel injection systems operated at high pressure. A leak not attended to can result in a significant fuel loss affecting mission time and increase the risk of fire. Consideration should be given to providing a means of early detection of leaks. | Inspectors should check for evidence that the licensee is adequately managing leaks. This should be visible to the naked eye, for example, staining of paintwork and condition of sumps and drip trays. |
| Air in the fuel system | Fuel systems should be provided with means of bleeding air from the fuel lines. | Air in the fuel system is most likely to occur following a maintenance and breakdown activity. Maintenance instructions and records should be examined to ensure that measures are in place and being implemented to ensure that air is removed from the system. |
| Ran out of fuel | Maintenance running of an EPG will reduce the amount of fuel remaining in the fuel tank. Tanks should be sized to provide sufficient fuel to achieve the mission time specified in the safety case. | Fuel tank levels should be inspected. Refuelling logs should confirm that fuel levels are always maintained above the minimum specified level. Instructions should identify at tank level refuelling requirements, to ensure sufficient reserves between reordering and refuelling, allowing for maintenance running. |
| High fuel level | An alarm should be provided to warn of overfilling. There should be a means of removing excess fuel. | Overfilling of the fuel tanks may be detrimental to the reliable operation of the EPG, for example, blocking of air filters on liquid fuel tanks may generate a vacuum as fuel levels drop. Refuelling logs should be inspected to ensure that refuelling is adequately controlled to ensure that tanks are not overfilled. |
| Controls not in auto | On completion of maintenance operations, EPGS controls should be reset to their normal (auto) state so that they will respond to any demand. Controls should be clear, unambiguous, and positioned where they can be readily seen. | Inspectors should ensure that this is identified in the maintenance instructions and recorded as completed in the relevant logs. Regular checks should also be carried out, to an appropriate timescale, to ensure that controls are always in the “auto” position during normal plant operation states. |
| Ancillary equipment | Inspectors should review the design of ancillary systems to ensure they cannot compromise the reliability of the principal EPG systems, for example: - heating, ventilation, and air conditioning (HVAC) system should ensure that suitable environmental conditions are maintained throughout the extreme weather events identified by the safety case. - a means of detecting leaks and build-up of liquids in drainage systems should be provided. - ancillary systems should be positioned and/or protected to ensure that they cannot present a threat to the principal EPG system. | Inspectors should review the ancillary equipment to confirm that it is being maintained in a satisfactory condition and does not present a potential threat to the principal EPG system, for example: - a faulty heating system may result in “clouding” of diesel fuel when external temperatures are very cold. - a significant quantity of diesel in a drainage system may present a fire risk. - a poorly secured item of equipment may become a projectile during a seismic event. |

# Appendix 2 – Guidance on the use of biodiesel

- There are several issues related to the use of biodiesel [12]. 
Licensees should be aware of these issues and have appropriate measures in place to address them. For example, Emergency DG manufacturers do not recommend the use of biodiesel for NPP standby application.

Biodiesel fuels contain less energy than petroleum derived diesel. This will affect the minimum fuel stock levels require by the safety case, operating rules, and operating instructions. Additional storage capacity may be required.

Biodiesel can have a cleaning effect that loosens accumulated sediment in fuel oil storage tanks. This sediment can then plug filters and other devices in the DG system thereby reducing reliability.

Biodiesel fuel has an affinity to absorb moisture and promote bacteria growth.

Biodiesel is biodegradable, and the presence of water, heat, oxygen, and other impurities accelerate degradation. Biodiesel might compromise DG reliability if it has been stored for an extended period.

EDGs may be preheated for standby mode applications. With biodiesel heating the fuel increases the risk of clogging of parts, injectors, and filters.

Biodiesel contains suspended particles of water from the manufacturing process. Over time, this water will fall out of suspension and form “dirty water” in the fuel oil storage tank, which eventually leads to the formation and growth of algae.

Biodiesel has different chemical characteristics from diesel and can interact with materials in a different way. It can corrode and tribologically attack metallic components and degrade elastomer parts. DG components may need to be replaced.

Brass, bronze, copper, lead, tin, and zinc in tanks and fittings can accelerate the oxidation process of biodiesel, creating solids, gels, and salts.

Biodiesels have higher cloud points (the temperature at which solid particles start to form, or gel) than conventional diesel. Clouding may also combine with suspended particles of water to prevent engine starting in cold temperature conditions.

Biodiesel is a solvent and might damage paint (for example, internal finishes of storage tanks).

# References

| [1] | ONR, “Safety Assessment Principles (SAPs) for Nuclear Facilities - 2014 Edition (Revision 1),” 2020. |
| --- | --- |
| [2] | ONR, “ONR-RD-REF-001 - An introduction to ONR’s technical assessment and inspection guides,” [Online]. |
| [3] | ONR, “NS-TAST-GD-019 Essential Services”. |
| [4] | ONR, “NS-TAST-GD-046 Computer Based Safety Systems”. |
| [5] | WENRA, “WENRA Safety Reference Levels for Existing Reactors 2020,” 2021. |
| [6] | IAEA, “IAEA Safety Standards - SSR-2/1 - Safety of Nuclear Power Plants: Design (Rev. 1)”. |
| [7] | IAEA, “IAEA Safety Standards, Design of Electrical Power Systems for Nuclear Power Plants. Specific Safety Guide. SSG-34”. |
| [8] | Amec Foster Wheeler, “ONR207 – National and International Good Practices for Diesel Generators (ONR record ref.: 2016/144561),” 2016. |
| [9] | Institute of Nuclear Power Operations (INPO), “Lessons Learned from the Nuclear Accident at the Fukushima Daiichi Nuclear Power Station (INPO 11-005 Addendum, Revision 0),” 2012. |
| [10] | ONR, “NS-TAST-GD-036 - Redundancy Diversity Segregation and Layout of Mechanical Plant”. |
| [11] | ONR, “NS-TAST-GD-013 - External Hazards”. |
| [12] | ONR, “OPEX Advice Note 002/09 - Biodiesel in Fuel Oil for Diesel Engines (ONR record ref.: 2009/200644),” 2009. |
| [13] | IAEA, “IAEA Safety Glossary - Terminology Used in Nuclear Safety, Nuclear Security, Radiation Protection,” 2018. |
| [14] | ONR, “NS-TAST-GD-017 - Annex 5 - Civil Engineering – Ageing Management and Damaged Structures”. |
| [15] | ONR, “Licence Condition Handbook,” 2017. |
| [16] | ONR, “ONR-RD-REF-002 - List of regulatory acronyms, abbreviations and initialisms,” [Online]. |

# Glossary

| Term | Description |
| --- | --- |
| Ageing | General process in which characteristics of an SCC gradually change with time or use [13]. |
| Arrangements (for operations) | The integrated set of infrastructural elements necessary to provide the capability for performing a specified function or task required to carry out a specified operation. The infrastructural elements may include authorities and responsibilities, organization, coordination, personnel, plans, procedures, facilities, equipment, or training [13]. |
| Design code | A standard with industry, national or international status, which defines the technical and organisational rules by which an item or process can be described and realised [1]. |
| Design life | The period during which a facility or component is expected to perform according to the technical specifications to which it was produced [13]. |
| Dutyholder | Any organisation or person that holds duties under legislation that ONR regulates. Dutyholders include: Licensees; Requesting Parties; Potential future Licensees; Operational Licence Dutyholders; Decommissioning site Licensees; New build site Licensees; budget holders; vendors; and supply chain members [14]. |
| Intelligent Customer | The capability of an organisation to understand where and when work is needed; specify what needs to be done; understand and set suitable standards; supervise and control the work; and review, evaluate and accept the work carried out on its behalf [1]. |
| Modification | Any alteration to buildings, plants, operations, processes or safety cases and includes any replacement, refurbishment or repairs to existing buildings, plants or processes and alterations to the design of plants during the period of construction [15]. |
| Safety case | The totality of a licensee’s (or dutyholder’s) documentation to demonstrate safety [1]. |
| Safety culture | The assembly of characteristics and attitudes in organisations and individuals which establishes that, as an overriding priority, protection and safety issues receive the attention warranted by their significance [13]. |
| Structures, Systems and Components (SSCs) | A general term encompassing all the elements (items) of a facility or activity that contribute to protection and safety, except human factors [13]. |

# List of key acronyms, initialisms and abbreviations

AC	Alternating current

C&I	Control and Instrumentation

CCF	Common Cause Failure

COTS	Commercial Off The Shelf [equipment]

DG	Diesel Generator

EIM&T	Examination Inspection Maintenance and Testing

EPG(s)	Emergency Power Generator(s)

EPGS(s)	Emergency Power Generation System(s)

GTG	Gas Turbine Generator

HVAC	Heating Ventilation and Air Conditioning

ICBM	Independent Confidence Building Measures

LOOP	Loss of Off-site Power

OEM	Original Equipment Manufacturer

NNP(s) 	Nuclear Power Plant(s)

SSC(s)	Structures, Systems and Component(s)

Note: A comprehensive list of regulatory acronyms, etc., can be found in ONR’s “List of regulatory acronyms, abbreviations and initialisms” [16].

# Document control information

Authored by: Nuclear Safety Inspector, Mechanical Engineering and Structural Integrity

Approved by: Head of Profession for Mechanical Engineering and Structural Integrity

Issue: 2.1

Published: March 2026

Next scheduled review: February 2028

Document reference: NS-TAST-GD-103

Revision commentary

| Issue | Description of update(s) |
| --- | --- |
| 2.1 | Minor update to content as part of a broader review to simplify guidance, where possible, across ONR’s TAGs. |

Template reference: ONR-DOC-TEMP-002 (Issue 6.1)

Warning: Inspectors should be aware that high pressure diesel systems present a serious conventional health risk. Fine, high velocity sprays can pass through the skin into body tissue.