ONR Technical Inspection Guide (TIG) LC 28 – Examination, Inspection, Maintenance and Testing (EIMT)

Contents

1.	Introduction	3

2.	Licence Condition 28: Examination, Inspection, Maintenance and Testing	4

3.	Purpose of the Licence Condition	5

4.	Guidance on arrangements for Licence Condition 28	6

5.	Guidance on inspection of arrangements and their implementation	7

Appendix A – Guidance for joint EIMT inspections	15

References	18

List of acronyms / initialisms	19

Document control information	20

# Introduction

Many licence conditions (LCs) require or imply that licensees establish arrangements to meet regulatory obligations. ONR inspects both compliance with the LCs and the adequacy of these arrangements. Most LCs are goal-setting and do not specify the content of arrangements, leaving licensees responsible for defining them and ensuring safety

## Purpose

ONR produces guides to assist inspectors to make regulatory judgements and decisions in relation to the adequacy of compliance, and the safety of activities on the site. This Technical Inspection Guide (TIG) has been prepared to support inspectors to judge the adequacy of LC compliance arrangements and implementation related to LC 28, the examination, inspection, maintenance and testing (EIMT) of plant important to safety.

LC 28 spans many topics, and this TIG does not duplicate detailed guidance available elsewhere, such as ONR’s nuclear safety Technical Assessment Guide (TAG) on EIMT [1] and International Atomic Energy Agency (IAEA) guidance (for example, [2]).

There is some alignment with LC 28 and relevant legislation for ONR’s other purposes (for example, nuclear security, safeguards, nuclear site health and safety), Appendix A contains further details of topics where there may be cross purpose inspection synergies. Consideration should also be given to opportunities to cooperate with other external regulators in joint inspections in accordance with obligations under the regulators’ code [3].

# Licence Condition 28: Examination, Inspection, Maintenance and Testing

28(1) 	The licensee shall make and implement adequate arrangements for the regular and systematic examination, inspection, maintenance and testing of all plant which may affect safety.

28(2) 	The licensee shall submit to ONR for approval such part or parts of the aforesaid arrangements as ONR may specify.

28(3) 	The licensee shall ensure that once approved no alteration or amendment is made to the approved arrangements unless ONR has approved such alteration or amendment.

28(4) 	The aforesaid arrangements shall provide for the preparation of a plant maintenance schedule for each plant. The licensee shall submit to ONR for its approval such part or parts of any plant maintenance schedule as ONR may specify.

28(5) 	The licensee shall ensure that once approved no alteration or amendment is made to any approved part of any plant maintenance schedule unless ONR has approved such alteration or amendment.

28(6) 	The licensee shall ensure in the interests of safety that every examination, inspection, maintenance and test of a plant or any part thereof is carried out:

  - by suitably qualified and experienced persons;

in accordance with schemes laid down in writing;

within the intervals specified in the plant maintenance schedule; and

under the control and supervision of a suitably qualified and experienced person appointed by the licensee for that purpose.

28(7) 	Notwithstanding the above paragraphs of this condition ONR may agree to an extension of any interval specified in the plant maintenance schedule.

28(8) 	When any examination, inspection, maintenance or test of any part of a plant reveals any matter indicating that the safe operation or safe condition of that plant may be affected, the suitably qualified and experienced person appointed to control or supervise such examination, inspection, maintenance or test shall bring it to the attention of the licensee forthwith who shall take appropriate action and ensure the matter is then notified, recorded, investigated and reported in accordance with arrangements made under Condition 7.

28(9) 	The licensee shall ensure that a full and accurate report of every examination, inspection, maintenance or test of any part of a plant indicating the date thereof and signed by the suitably qualified and experienced person appointed by the licensee to control and supervise such examination, inspection, maintenance or test is made to the licensee forthwith upon completion of the said examination, inspection, maintenance or test.

# Purpose of the Licence Condition

The purpose of LC 28, as expressed in sub-condition LC 28(1), is to ensure that all plant which may affect safety, receives regular and systematic EIMT. The purpose of this EIMT is to ensure the nuclear plant remains capable of performing its safety functions, with the required level of reliability.

A number of other LCs have interactions with LC 28. As detailed later, these include LC 6, LC 7, LC 12, LC 22, LC 24, LC 26 and LC 30.

# Guidance on arrangements for Licence Condition 28

LC 28 requires regular, systematic EIMT for all plant that may affect safety. ONR interprets plant as structures, systems and components (SSCs), including those with a direct safety role and those whose failure could impact safety.

Licensees typically divide maintenance catalogues into subsets, such as:

EIMT needed to meet safety case requirements (LC 23), forming the Plant Maintenance Schedule (PMS).

EIMT required by other legislation (for example, pressure systems, lifting equipment, environmental laws).

EIMT supporting operational reliability of plant without a direct safety function.

EIMT supporting decommissioning activities.

SSCs important to safety under LC 28 should be included in the PMS. 
The licensee’s arrangements must define how EIMT requirements are specified, controlled and changed. Where items of lower safety significance are excluded from the PMS, this must be justified, and adequate EIMT must still be carried out in line with LC 28(1).

PMSs were traditionally based on deterministic assessments of SSCs needed to meet the safety case, with EIMT specified to ensure reliability and keep the plant within its safety envelope. More recent PMSs also consider each SSC’s contribution to overall site risk as assessed by the PSA.

ONR may require approval of a high-level PMS section (the preface). 
Once approved, licensees may make changes to the main PMS through internal arrangements without further ONR approval. ONR currently approves PMS prefaces at reactor sites under LC 28(4).

The arrangements should ensure all EIMT on safety-related plant is:

performed by suitably qualified and experienced persons (SQEP);

completed in accordance with written schemes;

carried out within PMS-specified intervals;

controlled and supervised by an SQEP appointed by the licensee.

Under LC 1(1), “operations” includes maintenance, examination, testing and operation; therefore, written schemes for these activities fall under LC 24 operating instructions  [4]. Time intervals must be specified in the PMS, and failure to complete work within them constitutes non-compliance.

SQEP requirements for those supervising EIMT are described in the LC 12 TIG  [5]. TIG 26 also applies  [6], as EIMT activities are “operations” under LC 1(1). The supervising SQEP should form part of the licensee’s core safety capability as defined in  [7].

LC 1(1) defines ‘modification’ as any alteration to buildings, plant, operations, processes or safety cases. Therefore, changes to maintenance, examination or testing must be treated as modifications under the licensee’s LC 22 arrangements, and EIMT intervals may be altered through those arrangements.

The arrangements should also cover LC 28(8) requirements for notifying, recording, investigating and reporting defects or deficiencies found during EIMT.

Records of EIMT on SSCs affecting safety (LC 28(9)) must be compiled and retained under LC 6. These records demonstrate compliance with licence conditions as defined in LC 6(1). Further guidance is provided in the LC 6 TIG  [8] and the records management TAG  [9].

# Guidance on inspection of arrangements and their implementation

LC 28 covers a wide range of topics, with IAEA definitions of EIMT including both technical and administrative aspects  [10]. Key areas for LC 28 compliance inspections include:

the maintenance organisation;

the PMS;

implementation of EIMT;

supporting aspects such as spares and test equipment.

Table 1 provides further inspectable topics. Inspectors should apply a risk-informed approach when selecting which areas to examine.

Table 1 - LC 28 Inspection guidance

|  | Topic | Supporting guidance | Further guidance |
| --- | --- | --- | --- |
| 1 | Organisational Capability (links to LC 36) | The licensee’s organisation should have sufficient resources to implement the EIMT programme. This should include assigning roles and responsibilities associated with EIMT and identification of the resources required to fulfil the EIMT programme (for example, numbers of SQEP personnel from each engineering discipline). These should be captured on the nuclear baseline. | [2], [7] and [11] |
| 2 | Governance | The licensee should have appropriate governance and oversight of EIMT performance. This may be through use of metrics to monitor delivery of EIMT activities and trend backlogs or through governance of system health processes. | [2] |
| 3 | Interfaces between different groups | The licensee’s EIMT programme will involve interfaces between different groups (for example, operations, one or more engineering disciplines, radiation protection, contractors). The interfaces between these groups should be clear with roles and responsibilities and any handover arrangements defined. | [2] |
| 4 | SSC classification | The licensee’s arrangements should describe the methods and criteria for identifying the safety significance of all SSCs with clear linkage to the safety case. These SSCs may comprise the PMS. Where a graded approach is used there should be a proportionate approach within the arrangements for control of EIMT. If there are categories of lesser safety significant SSCs that are not included on the PMS (e.g. emergency equipment) then there should still be appropriate EIMT (a requirement of LC 28(1)). | [12] |
| 5 | EIMT requirements | The licensee’s PMS should state the EIMT required to support the safety case with the activity and frequency (including applicable tolerance(s)) underpinned and evidenced by suitable engineering substantiation and/or operational experience. This is also applicable for any lesser safety significant SSCs not included on the PMS. Where the contents of the PMS are based on demonstrations of operability/availability and continuing plant reliability, the EIMT activity identified should be sufficient to achieve adequate compliance with the assumptions contained in the site PSA. | [1] and [2] |
| 6 | PMS suspensions (links to LC 22) | Where an extension of the interval for EIMT is required, the licensee’s arrangements should set expectations for the level of justification as well as identify the potential need to request agreement from ONR under LC 28(7). If the PMS is not approved, then the intervals may be extended by following the licensee’s LC 22 arrangements. The arrangements should describe the appropriate control and authorisation measures with the justification for extensions giving consideration to operational experience and engineering substantiation. Note: If the licensee defers an LC 28 inspection they should confirm that they remain compliant with other legally binding inspection requirements (e.g. Pressure Systems Safety Regulations (2000) or Lifting Operations and Lifting Equipment Regulations 1998). |  |
| 7 | EIMT Modifications (links to LC 22) | The licensee should have an appropriate level of control on changes to EIMT for plant that may affect safety. The licensee’s arrangements should require a safety justification that is graded according to the safety significance of the SSC and in accordance with its LC 22 arrangements. |  |
| 8 | Periodic Shutdown (links to LC 30) | Where work activities that are specified in the PMS can only be carried out with the plant shutdown, the arrangements should define the maximum operating period between periodic shutdowns. In the case of operational reactor power stations, ONR has approved part of the maintenance schedule referred to as the ‘preface’ under LC 28(4). In such cases the preface specifies the duration of operation between periodic shutdowns. Therefore, should the licensee wish to permanently amend such an interval, as defined within the preface, its arrangements should reflect the requirement for an approval to be sought from ONR in accordance with LC 28(5). | [13] |
| 9 | Maintenance Optimisation | The licensee should have a process that uses operating experience (for example, from EIMT findings or defects) to optimise maintenance operations. For facilities where safety cases have been updated or renewed the licensee should review the PMS to ensure that the contents reflect the current safety case and hazard. | [2] |
| 10 | Ageing, degradation and obsolescence | The licensee’s arrangements should take consideration of asset management requirements (e.g. ageing, degradation, obsolescence) including the strategies for reviewing and managing the obsolescence of SSCs important to safety. EIMT methods and frequency of application should be effective in detecting or mitigating ageing and degradation mechanisms before they adversely impact safety. | [14] |
| 11 | Maintenance backlogs | The licensee should have a process to prevent maintenance backlogs and ensure any backlogs do not have an adverse effect on the safety of the plant. |  |
| 12 | Defects (links to LC7) | The licensee should have a process for reporting and investigating defects, determining the urgency and any remedial actions required to ensure continued safe operation of the plant. Defect records should identify the implications of the defect and appropriate corrective actions. |  |
| 13 | Condition monitoring | Condition monitoring can be used to inform the requirement for maintenance. This maybe through walkdowns at an appropriate frequency or by use of diagnostic methods. The licensee’s techniques and diagnostic methods need to be appropriate for the situation. The parameters to be monitored, the acceptance criteria and whether all potential failure modes are addressed should be clear. | [1] and [2] |
| 14 | Plant safety during maintenance | If plant is required to be taken out of service for EIMT then the minimum plant configuration should be specified by the licensee’s safety case and this should be defined as a condition / limit under LC 23. This may be informed by assessments of risk using PSA. The SSCs unavailability should be recorded, assessed and drawn to the attention of staff responsible for operating the plant. | [1] |
| 15 | Setting to work and workplace standards | Inspectors should consider inspecting EIMT work that is about to commence or is ongoing. Aspects of interest may include: - the setting to work briefing - confirming appropriate isolations and authorisation are in place for the work to commence (e.g. via a permit to work system) - the requirement for and adherence to foreign material exclusion controls - the use of test equipment that is in calibration - the written instructions in use. | [15] |
| 16 | SQEP (inc contractors) (links to LCs 10, 12 and 26) | The licensee’s arrangements should require that EIMT is carried out by SQEP (LC 28(6)(a)) and under the control and supervision of a SQEP person appointed for that purpose by the licensee (LC 28(6)(d)). Control and supervision arrangements should be reflective of the specific task and how the activity may affect wider safe operation of the plant. Licensees may use contractors to carry out EIMT. The licensee should act as the intelligent customer and check and approve the qualifications and experience of such workers prior to the work being authorised. The contractors should be SQEP for the work assigned. In order to determine the suitability of those undertaking EIMT work, consider discussions with person(s) carrying out work, their team leaders and section heads, as well as reviewing training/competence records. | [5], [6] and [7] |
| 17 | Written schemes (or procedures) (links to LC 24) | The licensee’s arrangements should require all activities to be carried out in accordance with written schemes (LC 28(6)(b)). There should be a clear auditable trail from the safety case to the specified EIMT requirements and the operating instruction. The procedures should be reflective of the safety significance of the SSC, appropriately categorised (e.g. reference vs continuous use) and used correctly. There should be consideration of potential shortfalls in human performance, quality assurance proportionate to the safety significance (e.g. use of independent verification checks & hold points) and a clear pass/fail criteria for the EIMT being undertaken. | [4] and [15] |
| 18 | Return to service | Following EIMT it is important that the plant/equipment/system is returned to service in a controlled manner with its operational functionality proven prior to reinstatement. SSCs that have had maintenance carried out should be reinstated, tested and accepted by an appropriate person (e.g. a duly authorised person appointed under LC 12(2)) before being declared operable and available. |  |
| 19 | Records (links to LC6) | Records (LC 28(9)) of EIMT carried out on SSCs which may affect safety should be compiled and retained in an appropriate manner by the licensee under its arrangements for compliance with LC 6. These should be commensurate with the safety significance of the SSCs to which they relate, reflecting the work completed, tasks left outstanding, and issues identified and should be signed off by the SQEP who controls and supervises the work. Where there are failures to meet PMS requirements these should be reported under LC 7 (LC 28(8) requirement). | [8] and [9] |
| 20 | Spares & Stores | Control of spares and appropriate storage is important in ensuring replacement SSC’s provide the required safety function. The licensee should have processes that ensure that correct stores items have been received, appropriately stored and with a suitable level of control on issue. This should include an acceptability check by a SQEP on receipt of the item and prior to use. The licensee should be able to demonstrate understanding of minimum stock levels required for critical spares, the shelf life for stored SSCs and any necessary environmental conditions for storage. Personnel should be aware of the potential for counterfeit, fraudulent and suspect items with arrangements in place, to quarantine, investigate and sentence suspect items. Replacement and configuration of plant items should be controlled with respect to design, specification, manufacture, function, procurement, storage, issue, fitness for purpose and installation. | [15], [16] and [17] |
| 21 | Test Equipment | Test equipment is used to confirm equipment is within calibration (or specification). Specific considerations for this topic include how the equipment is calibrated and controlled. This includes ensuring any equipment used is within calibration and the licensee’s controls over use of third party test equipment. Appropriate facilities for undertaking the testing should also be in place. |  |
| 22 | Specialisms | Specialisms may identify topics of interest or themes for inspections, through sub-divisional plans or based on operational experience. For example, corrosion management or the maintenance of passive components. |  |

# Appendix A – Guidance for joint EIMT inspections

Many LC 28 expectations align with other legislative requirements when SSCs serve both nuclear safety and other functions (for example, security, safeguards, site health and safety). This appendix highlights common areas to consider when planning LC 28 interventions.

Where such alignment exists, it may be appropriate to seek assurance on the system’s EIMT for relevant ONR purposes through a single, combined inspection.

- Safeguards

If a system provides both a nuclear safety and safeguards function, many LC 28 expectations also apply to compliance with the Nuclear Safeguards (EU Exit) Regulations 2019 (NSR19) and ONR’s Guidance for Nuclear Material Accountancy, Control and Safeguards (ONMACS)  [18]. 
NSR19 Regulation 6(1) requires operators to maintain an accountancy and control system for qualifying nuclear material at each facility. Guidance on EIMT for safeguards systems is provided in ONMACS, MACE 5.2.

Key aspects of MACE 5.2 that align with this TIG include:

Systems and components with an NMACS function should receive regular, systematic EIMT, supported by processes for in-service testing, inspection and maintenance. Where systems also support safety functions, this aligns directly with LC 28.

Maintenance requirements should be identified and included in an appropriate maintenance schedule. Licensees may use separate schedules for safety and safeguards, but all maintenance supporting either purpose must be captured.

EIMT frequency for safeguards or safety should reflect the required NMACS performance or claimed safety function. Safeguards may demand higher measurement precision than safety, requiring more frequent maintenance, while safety-critical equipment may require more rigorous EIMT due to potential consequences of failure.

When plant is taken out of service, arrangements must ensure enough equipment remains available to maintain safety as justified in the safety case. Likewise, safeguards operators must maintain NMACS capability at all times, applying compensatory measures when systems are offline.

Protective security

The Nuclear Industries Security Regulations (NISR) 2003  [19] require dutyholders to maintain an approved Security Plan (SP) and comply with its standards, procedures and arrangements. Plans are assessed and approved using the Security Assessment Principles (SyAPs) framework, supported by TAGs such as CNS-TAST-GD-5.2 for EIMT  [20].

The relevant SyAPs [21] section is Security Delivery Principle (SyDP) 5.2 – Examination, Inspection, Maintenance and Testing, part of Fundamental Security Principle (FSyP) 5 on reliability, resilience and sustainability. SyDP 5.2 (para. 147) states that:

“A process for in-service testing, inspection and other maintenance procedures of security structures, systems and components should be identified in the security plan.”

Inspecting EIMT of security SSCs is one area in which joint inspections and specialist support would be beneficial. ONR’s Nuclear Security Inspections TIG (CNS-INSP-GD-001) (Ref. [22]) encourages security inspectors to consider a cross-purpose approach for FSyP 5 (Section 4.3, paragraph 37).

SyAPs (para.150) states that:

“EIMT is part of normal operation and it should be possible to carry out these tests without any loss of any security function.”

Although this may seem obvious, there have been cases where security functions were unintentionally disabled during EIMT on non-security SSCs (e.g., isolating an electrical board that also powers the Perimeter Intrusion Detection System). Such errors typically arise from stove-piped EIMT arrangements and inadequate supervision or control of security-related EIMT. To prevent these safety and security risks, an integrated dutyholder approach to EIMT is essential.

SyAPs (para.150) states that:

“…the potential for EIMT to be exploited by an adversary should be analysed and the risks so arising mitigated.”

Security inspectors consider deliberate, malicious acts that could lead to sabotage or theft of nuclear or other radioactive material. Safety inspectors should share planned EIMT inspection scope with the site Security Inspector, who can confirm whether SSCs have security relevance. 
One example is applying a “two-person rule” for maintenance on critical systems vulnerable to insider sabotage.

Inspectors should also check that security is routinely embedded in the dutyholder’s EIMT arrangements. This may include:

advance notice of EIMT affecting security-related SSCs, allowing contingency planning or submission of a Temporary Security Plan to ONR;

recognising that EIMT on one safety SSC may increase the security importance or vulnerability of another, requiring dynamic security measures such as temporary armed guarding.

Where any security aspect is involved, the first point of contact should be the site Security Inspector.

- Cyber security

As operational technology becomes more widespread on nuclear sites, EIMT requirements may be shaped by both nuclear safety and cyber security needs. This is likely to increase the need and opportunities for joint inspections where equipment requires EIMT to satisfy both LC 28 and cyber security requirements.

Site safety

EIMT may be required on SSCs to meet both nuclear safety and health and safety legislation, creating opportunities to inspect LC 28 compliance alongside conventional safety requirements. Examples include lifting equipment and pressure systems that must be maintained under their respective regulations.

There are also opportunities for themed inspections where LC 28 and wider maintenance topics are reviewed together. For example, a maintenance-themed inspection could include control of work and the permit-to-work system, both important for protecting personnel undertaking maintenance activities.

# References

| [1] | ONR, NS-TAST-GD-009, Examination, Inspection, Maintenance & Testing of Items Important to Safety. |
| --- | --- |
| [2] | IAEA, SSG-74, Maintenance, Testing, Surveillance and Inspection in Nuclear Power Plants. |
| [3] | GOV, “Department for Business Innovation & Skills, Regulators’ Code, April 2014.”. |
| [4] | ONR, NS-INSP-GD-024 - LC 24 Operating Instructions. |
| [5] | ONR, NS-INSP-GD-012, LC 12 Duly authorised and other suitably qualified and experienced person. |
| [6] | ONR, NS-INSP-GD-026, LC 26 Control and Supervision of Operations. |
| [7] | ONR, NS-TAST-GD-049, Licensee Use of Contractors and Intelligent Customer Capability. |
| [8] | ONR, NS-INSP-GD-006, LC 6 Documents, Records, Authorities and Certificates. |
| [9] | ONR, NS-TAST-GD-033, Licensee Management of Records. |
| [10] | IAEA Nuclear Safety and Security Glossary - Terminology Used in Nuclear Safety, Nuclear Security, Radiation Protection and Emergency Preparedness and Response, 2022 (Interim) Edition. |
| [11] | ONR, NS-TAST-GD-065, Function and Content of the Nuclear Baseline. |
| [12] | ONR, NS-TAST-GD-094, Categorisation of Safety Functions and Classification of Structures, Systems and Components. |
| [13] | ONR, NS-INSP-GD-030, LC 30 - Periodic Shutdown. |
| [14] | ONR, NS-TAST-GD-109, Ageing and Degradation Management. |
| [15] | ONR, NS-TAST-GD-102, General Guidance for Mechanical Engineering Specialism Group. |
| [16] | ONR, NS-TAST-GD-077, Supply Chain Management Arrangements for the Procurement of Nuclear Safety Related Items or Services. |
| [17] | ONR Advice Note, Supply Chain Management - Counterfeit, Fraudulent and Suspect Items (CFSI, 2022/73725). |
| [18] | ONR Nuclear Material Accountancy, Control, and Safeguards, ONR-CNSS-MAN-001. |
| [19] | HMG, Nuclear Industries Security Regulations 2003/403. |
| [20] | ONR, CNS-TAST-GD-5.2 - Examination, Inspection, Maintenance and Testing of Physical Protection Systems. |
| [21] | ONR, Security Assessment Principles for the Civil Nuclear Industry, 2022 Edition, Version 1. |
| [22] | ONR, CNS-INSP-GD-001 - Nuclear Security Inspections. |
| [23] | ONR, SG-INSP-GD-001, Safeguards. |

# List of acronyms / initialisms

| Acronym / initialism | Description |
| --- | --- |
| EIMT | Examination, Inspection, Maintenance and Testing |
| FSyP | Fundamental Security Principle |
| IAEA | International Atomic Energy Agency |
| LC | Licence Condition |
| MACE | Material Accountancy and Control Expectation |
| NISR | Nuclear Industries Security Regulations 2003 |
| NMACS | Nuclear Material Accountancy, Control, and Safeguards |
| NSR19 | The Nuclear Safeguards (EU Exit) Regulations 2019 |
| ONMACS | ONR Guidance for Nuclear Material Accountancy, Control and Safeguards |
| ONR | Office for Nuclear Regulation |
| PMS | Plant Maintenance Schedule |
| PSA | Probabilistic Safety Assessment |
| SQEP | Suitably Qualified and Experienced Person |
| SSC | Structure, System and Component |
| SP | Security Plan |
| SyAPs | Security Assessment Principles |
| SyDP | Security Delivery Principle |
| TAG | Technical Assessment Guide |
| TIG | Technical Inspection Guide |

# Document control information

Authored by: Nuclear Safety Inspector

Approved by: Head of Profession for the Operational Inspection Specialism

Issue: 9.2

Published: June 2026

Next scheduled review: October 2028

Document reference: NS-INSP-GD-028

Record reference: ONRHH-822789359-20584

Revision commentary

| Issue | Description of update(s) |
| --- | --- |
| 9 | Guidance on inspection of arrangements and implementation of them revised. TIG moved to latest template. |
| 9.1 | TIG moved to the latest template and check of content. No significant changes to the guidance. |
| 9.2 | Error corrected in reproducing the LC and its clauses in section 2 of this guidance. |

Template reference: ONR-DOC-TEMP-003