Office for Nuclear Regulation (ONR)
Site Report for
Hinkley Point B Site

Report for period 1 April to 30 June 2022

Foreword
This report is issued as part of ONR's commitment to make information about inspection and regulatory activities relating to the above site available to the public. Reports are distributed to members for the Site Stakeholder Group and are also available on the ONR website (http://www.onr.org.uk/llc/).
Site inspectors from ONR usually attend Site Stakeholder Group meetings where these reports are presented and will respond to any questions raised there. Any person wishing to inquire about matters covered by this report should contact ONR.

Table of Contents

Inspections
  1. Dates of Inspection
The ONR site inspector made inspections on the following dates during the report period:
- 12 April 2022 (COMAH)
- 24 to 26 May (LC17 – Spares Management)

Routine Matters
  1. Inspections
Inspections are undertaken as part of the process for monitoring compliance with:
- the conditions attached by ONR to the nuclear site licence granted under the Nuclear Installations Act 1965 (NIA65) (as amended);
- the Energy Act 2013
- the Health and Safety at Work etc Act 1974 (HSWA74); and
- regulations made under HSWA74, for example the Ionising Radiations Regulations 2017 (IRR17) and the Management of Health and Safety at Work Regulations 1999 (MHSWR99).
The inspections entail monitoring the licensee’s actions on the site in relation to incidents, operations, maintenance, projects, modifications, safety case changes and any other matters that may affect safety. The licensee is required to make and implement adequate arrangements under the conditions attached to the licence in order to ensure legal compliance. Inspections seek to judge both the adequacy of these arrangements and their implementation.
In this period, routine inspections of Hinkley Point B Power Station covered the following:
Control of Major Accident Hazards (COMAH)
This inspection was a joint inspection carried out by a specialist ONR inspector with the Environment Agency Site Inspector. COMAH regulations are in place to ensure that major accident risks from conventional hazards are adequately controlled. This inspection was targeted at assessing the adequacy of COMAH regulatory compliance within decommissioning planning and preparation activities.
The key regulatory activities undertaken are summarised below:
- Review management system arrangements;
- Review control of hazardous substance inventory and projected substance reduction during decommissioning;
- Review arrangements for decommissioning planning and preparation, including incorporation of COMAH requirements;
- Inspect standard of COMAH substance bulk storage at HPB.
The inspector was content with the outcome of the management system element of the inspection and was of the opinion that the inventory of hazardous substances is being adequately managed within COMAH lower tier threshold boundaries.
# Planning for the removal of COMAH substances following end of generation and achieving fuel free verification (FFV) was explored. Through post generation plant review work, the dutyholder identified systems and substances no longer required and also those remaining in service until FFV. Together with the engineering change framework and asset care strategy, it was evident decommissioning planning is progressing through a structured approach. Whilst this is acknowledged, the inspector concluded planning regarding prioritisation and resourcing for the removal of COMAH substances requires development. In particular, clarity regarding the safe state / end-of-life condition of COMAH vessels and pipework before transfer to the Nuclear Decommissioning Authority.
# The inspector sampled COMAH substance storage areas during the plant walk down and judged standards observed to be good.
# During the inspection the inspector identified a number of issues judged to be minor, requiring follow up action or provision of additional information, but none that warranted placing of a formal regulatory issue.

An inspection rating of Green, no formal action was assigned to this intervention.

Management Systems (Spares)
The aim of this inspection was to determine what arrangements are in place for the identification and retention of spares, the implementation of these on site and how these will change in the move from generation to defuelling.
The dutyholder has arrangements for the identification and tracking of spares which are important from a safety and commercial perspective. However I noted that there was no formal KPI that showed how this process was performing. The Supply Chain Manager demonstrated the ability to run reports that could be used as the basis of a KPI. I sampled the reports and did not identify any shortfalls that would have a direct safety consequence
I concluded that although there was a shortfall identified over the monitoring of spares, in general the dutyholder could demonstrate that the spares holdings for defuelling had been assessed and that work was underway to address any spares shortfalls. I considered a level 4 issue to be appropriate for the monitoring of spares going forward. Overall I concluded that the inspection should be rated as ‘green’.

  1. Other Work
Although there continues to be risks from the coronavirus pandemic during the reporting period visits to site have now returned to normal. ONR will continue to monitor the situation and adapt its approach as necessary.
Non-Routine Matters
Licensees are required to have arrangements to respond to non-routine matters and events. ONR inspectors judge the adequacy of the licensee’s response, including actions taken to implement any necessary improvements.
Reactor Trips
Following on from the automatic trip reported in the last quarterly report, there was a repeat automatic trip of R3 due to low pressure on a turbine 7 intermediate pressure governor valve. The reactor shutdown safely and post-trip cooling was established. The investigation is ongoing, but initial indications are that the lessons from the previous trip were not fully learned and there appears to have been a series of small historical errors, that have resulted in the hoses and connectors for the pressure system not being able to withstand the pressures experienced by the system. The hoses and connectors were not safety mechanisms and therefore do not fall under the full requirements of LC28.
Safety Mechanism not Calibrated
The Maintenance Schedule for Hinkley Point B identifies various items of equipment that are required to be maintained in order to meet the requirement of LC28. ONR consider these items as safety mechanisms. The Maintenance Schedule includes a number of RADOS monitors that are used to check personnel for contamination. This RADOS monitor was used on exiting the pile cap. Although the radiological consequences of not calibrating this single monitor are relatively small, the system for ensuring Safety Mechanisms are maintained is important for nuclear safety. ONR are awaiting the dutyholder’s investigation report before deciding whether any further action is required.
Regulatory Activity
ONR may issue formal documents to ensure compliance with regulatory requirements. Under nuclear site licence conditions, ONR issues regulatory documents, which either permit an activity or require some form of action to be taken; these are usually collectively termed ‘Licence Instruments’ (LIs) but can take other forms. In addition, inspectors may take a range of enforcement actions, to include issuing an Enforcement Notice.
- Two Licence Instruments were issued this period.
- No Enforcement Notices or Enforcement letters were issued during this period.
Table 1: Licence Instruments and Enforcement Notices Issued by ONR during this period
Date	Type	Ref. No.	Description
11/05/2022	Agreement	LI570	Application for Agreement, LC30(2) extension of the operating period of Hinkley Point B Site Reactor 4 from 24 May 2022 to 31 July 2022
11/5/2022	Approval	LI571	The substitution of Maintenance Schedule Preface HINB/MS/PREFACE Revision 003 dated April 2022 for Maintenance Schedule Preface HINB/MS/PREFACE Revision 001 dated 28 August 2009.

The agreement aligns the end of the operating period to the planned end of generation. ONR were of the opinion that shutting down the reactors for a full statutory outage two months prior to end of generation was not proportionate.
The approval allows the duty holder to defer future outages without a formal agreement from ONR. This is limited by certain constraints on duration and periods of operation and any changes are subject to the requirements of change control under LC22, which gives ONR visibility of any ongoing deferments.
Reports detailing the above regulatory decisions can be found on the ONR website at http://www.onr.org.uk/pars/.

News from ONR
For the latest news and information from the Office for Nuclear Regulation, please read and subscribe to our regular email newsletter ‘ONR News’ at www.onr.org.uk/onrnews

Contacts
Office for Nuclear Regulation
Redgrave Court
Merton Road
Bootle
Merseyside
L20 7HS
website:	www.onr.org.uk
email:	Contact@onr.gov.uk
This document is issued by the Office for Nuclear Regulation (ONR). For further information about ONR, or to report inconsistencies or inaccuracies in this publication please visit http://www.onr.org.uk/feedback.htm.
© Office for Nuclear Regulation 2023
If you wish to reuse this information visit www.onr.org.uk/copyright.htm for details.
Published 1/23
For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled.