ONR Site Report EDF Energy – Hunterston B

ONR Site Report

EDF Energy - Hunterston B

Report for period: 1 July 2025 to 31 December 2025

Authored by: Nominated Site Inspector

Approved by: Head of Regulation, Decommissioning Fuel and Waste

Issue: 1

Published: February 2026

Record reference: 2026/4312

Foreword

This report is issued as part of our commitment to make information about inspection and regulatory activities relating to the above site available to the public. Reports are distributed to members of the Hunterston Site Stakeholder Group and are also available on our website.

Our site inspectors usually attend Hunterston Site Stakeholder Group meetings where these reports are presented and will respond to any questions raised there. Any person wishing to inquire about matters covered by this report should contact  us via email at contact@onr.gov.uk.

Contents

1.	Inspections	4

2.	Routine matters	4

3.	Non-routine matters	5

4.	Regulatory activity	6

5.	News from ONR	7

6.	Contacts	7

References	7

# Inspections

## Date(s) of inspection

Our site inspector and specialist inspectors made inspections and site visits on the following dates during the report period 1 July 2025 to 31 December 2025:

- 1-5 September 2025

- 15-20 September 2025

- 8-9 October 2025

- 10-13 November 2025

- 17-18 December 2025

# Routine matters

## Inspections

Inspections are undertaken as part of the process for monitoring compliance with:

the conditions attached by ONR to the nuclear site licence granted under the Nuclear Installations Act 1965 (NIA65) (as amended);

the Energy Act 2013;

the Health and Safety at Work etc Act 1974 (HSWA74);

the Nuclear Industries Security Regulations 2003 (as amended); and

regulations made under HSWA74, for example the Ionising Radiations Regulations 2017 (IRR17) and the Management of Health and Safety at Work Regulations 1999 (MHSWR99).

The inspections entail monitoring the licensee’s actions on the site in relation to incidents, operations, maintenance, projects, modifications, safety case changes and any other matters that may affect safety. The licensee is required to make and implement adequate arrangements under the conditions attached to the licence in order to ensure legal compliance. Inspections seek to judge both the adequacy of these arrangements and their implementation.

In this period, routine inspections of, and site visits to Hunterston B covered:

- The Control of Major Accident Hazard (COMAH) Regulations, 2015.

- Preparations for site transfer from EDF Energy  to Nuclear Restoration Services Limited (NRS)

- Site Emergency Preparedness

- Implementation of the deconstruction organisation

- Electrical safety under the Electricity at Work Regulations, 1989

- COMAH Inspection – Hunterston B is no longer a COMAH site

- The ONR and the Scottish Environmental Protection Agency (SEPA) jointly constitute the COMAH Competent Authority. On 15 July 2025, Hunterston B submitted a COMAH denotification, declaring that their holdings of dangerous substances had decreased below the COMAH lower tier threshold. Our inspectors, with their SEPA counter-part conducted a COMAH inspection on 4 September 2025 to review the site’s approach to removing dangerous substances, verify the removal of COMAH-relevant dangerous substances below the lower tier threshold, and review the control of any residual risk. From the areas sampled, the approach taken by the site to remove dangerous substances was judged to meet the legal requirement for compliance with COMAH regulations. The dangerous substances inventory was judged to be below the lower tier threshold, and the residual risk was judged to be adequately controlled.

- Preparations for site transfer from EDF Energy to NRS

During the site visits in September, October and November, our inspectors observed activities conducted by EDF Energy to refocus personnel onto the changed on-site hazard profile, and ‘shadow working’ activities to demonstrate how those arrangements that will change at point of transfer will be implemented. Each of the activities observed was judged to be adequate, which contributes to informing our  decision on whether to re-license the site to NRS on 1 April 2026.

- Site Emergency Preparedness Demonstration

- In this reporting period, ONR agreed to, and issued a Licence Instrument (LI) (LI-576) under Licence Condition (LC) 11 for, the revised emergency plan on 25 July 2025.

- On 12 November 2025, our inspectors evaluated a demonstration of the station emergency arrangements. The emergency exercise was judged to be an adequate and effective challenge to the emergency response arrangements required under LC 11. As with all exercises, some learning opportunities were identified – in this case, greater familiarity in the use of emergency equipment and in casualty handling for elements of the emergency response teams.

- Implementation of the Deconstruction Organisation

- On 17 July 2025, ONR agreed to the implementation of, and issued an LI (LI-577) under LC 22 for, the post defuelling safety case.

- During the reporting period, the site fully implemented the post defueling safety case, the revised Site Security Plan (SSP) for a fuel free site, and new emergency arrangements for a fuel free site. The site successfully transitioned to its decommissioning organisational structure on 30 September 2025.

- Our inspectors reviewed the implementation of the organisational changes on 17 December 2025. Areas of good practice were identified in the Construction Office, with adequate control of work to ensure that only suitably qualified and exerienced persons perform any duties which may affect the safety of operations on the site.  More widely, however, we identified shortfalls in the management of the organisation and in the management of competence of personnel.  We are supporting site in addressing these issues prior to transfer.

- Electrical safety under the Electricity at Work Regulations, 1989

- On 11 November 2025, Hunterston B reported an electrical safety event to ONR and subsequently site initiated a significant adverse condition investigation.

- An electrical safety specialist and the nominated site inspector conducted enquiries into the event and site’s response to it on 18 December 2025.  These enquiries identified significant shortfalls against the requirements of the Electricity at Work Regulations, 1989. We will take the necessary regulatory action to ensure these shortfalls are addressed. Further details on the action taken will be reported in our next report to the SSG.

## Other work

Our site inspectors attended the SSG on 4 September 2025 and on 4 December 2025.

# Non-routine matters

Licensees are required to have arrangements to respond to non-routine matters and events. Our inspectors judge the adequacy of the licensee’s response, including actions taken to implement any necessary improvements.

There were no such matters or events of significance during the period.

# Regulatory activity

We may issue formal documents to ensure compliance with regulatory requirements. Under nuclear site licence conditions, we issue regulatory documents, which either permit an activity or require some form of action to be taken; these are usually collectively termed ‘Licence Instruments’ (LIs) but can take other forms. In addition, inspectors may take a range of enforcement actions, to include issuing an enforcement notice.

The LIs detailed below were issued to Hunterston B in this reporting period.

No enforcement notices were issued to Hunterston B in this reporting period.

Table 1: Licence Instruments issued by ONR during this period

| Date | Type | Reference | Description |
| --- | --- | --- | --- |
| Jul 2025 | LI | LI-577 | Post Defuelling Safety Case |
| Jul 2025 | LI | LI-576 | Emergency Arrangements |

Reports detailing the above regulatory decisions can be found on our  website.

.

# News from ONR

For the latest news and information from us, please read and subscribe to our regular email newsletter ‘ONR News’ at https://www.onr.org.uk/news/newsletter/.

# Contacts

Office for Nuclear Regulation

Redgrave Court

Merton Road

Bootle

Merseyside

L20 7HS

website: www.onr.org.uk

email: 	Contact@onr.gov.uk

This document is issued by ONR. For further information about us, or to report inconsistencies or inaccuracies in this publication please email us via contact@onr.gov.uk.

If you wish to reuse this information visit  https://www.onr.org.uk/access-to-information/copyright/ for details.

For published documents, the electronic copy on our website remains the most current publicly available version and copying or printing renders this document uncontrolled.

# References

There are no sources in the current document.