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Foreword
This report is issued as part of our commitment to make information about inspection and regulatory activities relating to the above site available to the public. Reports are distributed to members for the Dungeness site stakeholder group and are also available on our website: www.onr.org.uk/publications/regulatory-reports/site-specific-reports/llcssg-reports.
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Our site inspectors usually attend Dungeness site stakeholder group meetings where these reports are presented and will respond to any questions raised there. Any person wishing to inquire about matters covered by this report should contact us via email at contact@onr.gov.uk.
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[bookmark: _Toc109727647]Date(s) of inspection
Our site inspector and other specialist inspectors made inspections/site visits on the following dates during the report period 1 April – 31 August 2026. This period has been adjusted from typical quarterly/six monthly ONR reporting to support the Dungeness B Site Stakeholder Group frequency. The next report will cover inspection activity from 01 September 2026:
22 April 
6 May
21-22 May
11 June
7-9 July 
26 August
[bookmark: _Toc95889183][bookmark: _Toc180135449]Routine matters
Inspections 
Inspections are undertaken as part of the process for monitoring compliance with: 
The conditions attached by ONR to the nuclear site licence granted under the Nuclear Installations Act 1965 (NIA65) (as amended); 
The Energy Act 2013;
The Health and Safety at Work etc Act 1974 (HSWA74); and 
Regulations made under HSWA74, for example, the Ionising Radiations Regulations 2017 (IRR17) and the Management of Health and Safety at Work Regulations 1999 (MHSWR99).
The inspections entail monitoring the licensee’s actions on the site in relation to incidents, operations, maintenance, projects, modifications, safety case changes and any other matters that may affect safety. The licensee is required to make and implement adequate arrangements under the conditions attached to the licence in order to ensure legal compliance. Inspections seek to judge both the adequacy of these arrangements and their implementation.
In this period, routine inspections of Dungeness B covered the following: 
Emergency arrangements
Examination inspection maintenance and testing
conventional (non-nuclear) health and safety 
security 
Emergency Arrangements
ONR assessed the licensee’s demonstration of its emergency arrangements through a Level 1 exercise at Dungeness B. The exercise provided an appropriate level of challenge and enabled inspectors to sample the effectiveness of command, control, communication and operational response arrangements under demanding conditions. Overall, the licensee demonstrated areas of effective implementation and broadly achieved the intent of the exercise. However, ONR identified shortfalls in aspects of the emergency response, including the management and coordination of some response activities. These shortfalls indicated that the arrangements were not implemented to the standard expected in all areas. On balance, ONR judged the licensee’s performance to be not adequate and rated the inspection Amber, requiring improvement -  an enforcement letter has been sent to site to this effect (see Regulatory Activity section).  
LC28 Examination inspection maintenance  and testing
ONR inspected the licensee’s arrangements for examination, inspection, maintenance and testing, focusing on the management of fuel route system reliability and associated single point vulnerabilities at Dungeness B. The inspection considered the adequacy of arrangements and their implementation through discussions with station personnel, review of relevant evidence and inspection of facilities. Overall, the licensee demonstrated that arrangements were in place to support the continued reliability of the fuel route system and to manage associated vulnerabilities. ONR identified examples of effective practice, together with some minor observations, which were shared with the site for consideration. Based on the evidence sampled, ONR judged that the licensee had adequately managed fuel route system reliability and associated vulnerabilities. Accordingly, ONR rated the inspection Green, with no formal action required
Construction Design Management and Fire Safety
ONR inspected the licensee’s arrangements for compliance with construction design management and fire safety requirements, focusing on the new administration building project at Dungeness B. The inspection considered the adequacy of arrangements and their implementation through discussions with station personnel and review of relevant documentary evidence. Overall, the licensee demonstrated that appropriate arrangements were in place to support compliance with the Construction (Design and Management) Regulations 2015 and the Regulatory Reform (Fire Safety) Order 2005, taking account of the current stage of the project. ONR identified one shortfall associated with the demonstration of principal designer appointment arrangements, which is being tracked through a regulatory issue. Based on the evidence sampled, ONR judged that the licensee’s arrangements were adequate. Accordingly, ONR rated the inspection Green.
Members of the public who would like further information on our inspection activities during the reporting period can view site inspection records on our website: www.onr.org.uk/publications/regulatory-reports/site-specific-reports/inspection-records.
Should you have any queries regarding our inspection activities, please email contact@onr.gov.uk.
Other work
The site inspector met regularly with the site-based Independent Nuclear Assurance (INA) team to ensure the internal regulator function remains effective and verifying information provided by the station. 
The site inspector undertook a number of intelligence gathering activities and plant visits including engagement with members of the site’s senior leadership team and the site’s safety representatives.
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Licensees are required to have arrangements to respond to non-routine matters and events. Our inspectors judge the adequacy of the licensee’s response, including actions taken to implement any necessary improvements. 
On 6 May during demolition of a redundant concrete base a digger operator suffered a facial injury as a result of being struck by a piece of concrete debris. Although the incident did not meet formal ONR or RIDDOR incident reporting criteria ONR follow up of the incident identified shortfalls with respect to compliance with the Provision and Use of Work Equipment Regulations 1998 and has served an enforcement letter on Dalkia Facilities Ltd (see Regulatory Activity section). ONR inspectors will follow up effectiveness of identified improvement activities as part of normal regulatory business.
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We may issue formal documents to ensure compliance with regulatory requirements. Under nuclear site licence conditions, we issue regulatory documents, which either permit an activity or require some form of action to be taken. These are usually collectively termed licence instruments but can take other forms. In addition, inspectors may take a range of enforcement actions, to include issuing an enforcement notice. 
The following licence instruments, enforcement notices and enforcement letters have been issued during the period: 
Table 1: Licence instruments and enforcement notices issued by ONR during this period 
	Date 
	Type 
	Reference 
	Description 

	01/06/2026
	Enforcement letter 
	 DNB71388R 
	Letter regarding shortfalls observed during exercise MAVEN

	24/08/2026 
	Enforcement Letter
	 GEN71478N
	Letter to Dalkia Facilities Ltd in response to an event  resulting in injury to operative during work at Dungeness B Power Station
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For the latest updates and information on our work, please subscribe to our regular email newsletter, ONR News, at www.onr.org.uk/news/newsletter.
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Office for Nuclear Regulation
Redgrave Court
Merton Road
Bootle
Merseyside
L20 7HS
Website: www.onr.org.uk
Email: contact@onr.gov.uk
This document is issued by ONR. For further information about us, or to report inconsistencies or inaccuracies in this publication, please email contact@onr.gov.uk. 
If you wish to reuse this information, please visit www.onr.org.uk/access-to-information/copyright blocked::blocked::BLOCKED::http://www.hse.gov.uk/copyrightfor details. 
For published documents, the electronic copy on our website remains the most current publicly available version and copying or printing renders this document uncontrolled.
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