ONR Project assessment report PR-02211 – Torness Reactor 2 Periodic Shutdown - S13R2

ONR Project assessment report

Project name: PR-02211

Report title: Torness Reactor 2 Periodic Shutdown - S13R2

Dutyholder/Applicant: EDF Energy Nuclear Generation Limited

Report issue no.: 1

Publication date: May 2026

Document ID: ONRW-2019369590-27894

© Office for Nuclear Regulation, [2026]

For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled. If you wish to reuse this information visit www.onr.org.uk/copyright for details.

# Executive summary

Title

Torness reactor 2 periodic shutdown S13R2

Permission Requested

EDF Energy Nuclear Generation Limited (the licensee) has asked us for consent to start-up Torness Reactor 2 after the S13R2 periodic shutdown.

Background

The nuclear site licence for Torness requires the licensee to shutdown any plant or process for the purpose of Examination, Inspection, Maintenance or Testing (EIMT) in accordance with the requirements of the plant maintenance schedule. The maintenance schedule preface specifies that reactor periodic shutdowns take place after a maximum period of three calendar years from consent to start-up after the previous periodic shutdown.

We gave consent to start-up reactor 2 after its last periodic shutdown on 25 July 2022. Therefore, it was required to shutdown on or before 25 July 2025. However, in order to de-conflict the periodic shutdown programme for 2024/2025, and minimise the impact of supply chain resource availability, we gave our agreement to extend the operating period of reactor 2 until no later than 9 February 2026. Reactor 2 was shutdown on 19 January 2026 for its periodic shutdown (denoted as S13R2) with a planned duration of 80 days.

Assessment and inspection work carried out by ONR in consideration of this request

A targeted sample of the activities and documentation produced by the licensee for the S13R2 periodic shutdown and the EIMT of structures, systems and components important to nuclear safety have been assessed and / or inspected by our specialist inspectors from graphite structural integrity, teel structural integrity, electrical engineering, control and instrumentation, mechanical engineering and civil engineering.

The Scottish Environment Protection Agency was consulted and did not have any objections to us granting consent for reactor 2 to start-up. Our civil nuclear security were also consulted and had no security concerns regarding the start-up of reactor 2.

Matters arising from ONR's work

There are no outstanding matters arising from our assessment and inspection activities.

Conclusions

Our assessment and inspections of the Torness reactor 2 outage have concluded that:

the EIMT requirements specified in plant maintenance schedule in support of LC30 have been complied with;

the EIMT has been carried out by suitably qualified and experienced persons, with an appropriate level of supervision and quality assurance commensurate with the equipment’s safety function; and

safety issues identified by the licensee during the shutdown have been adequately addressed with suitable and sufficient safety justification that the relevant safety case limits and conditions are not challenged.

We are content that all necessary work has been completed, subject to those activities that must be delayed until the reactor is pressurised or will be carried out during the restart. The remaining information will be reported to us in the 28-day report, or in specific documents that are not required prior to granting consent.

In conclusion, we have not identified any matters that would prevent us from granting consent for Torness reactor 2 to start-up after the S13R2 periodic shutdown.

Recommendation

We should issue licence instrument 569 under LC 30 for nuclear site licence number Sc.14, granting consent to start-up Torness Reactor 2.

Table 1: List of abbreviations.

| Term/Acronym | Description |
| --- | --- |
| ALARP | As low as reasonably practicable |
| APEX | Appointed examiner |
| C&I | Control and instrumentation |
| EC | Engineering change |
| EIMT | Examination, inspection, maintenance or testing |
| INA | Independent nuclear assurance |
| INSA | Independent nuclear safety assessment |
| LC | Licence condition |
| OAP | Outage assessment panel |
| ONR | Office for Nuclear Regulation |
| PCPV | Pre-stressed concrete pressure vessel |
| PSSR | Pressure systems safety regulations 2000 |
| R2 | Reactor 2 |
| SEPA | Scottish environment protection agency |
| SQEP | Suitably qualified and experienced persons |
| SSC | Structure, system and component |
| TOR | Torness |

Table of contents

Executive summary	4

1.	Permission requested	8

2.	Background	8

3.	Assessment and inspection work carried out by ONR in consideration of this request	8

3.1.	Graphite structural integrity	9

3.2.	Steel structural integrity	10

3.3.	Electrical engineering	11

3.4.	Control and instrumentation	12

3.5.	Mechanical engineering	13

3.6.	Civil engineering	13

3.7.	Early outage safety review	14

3.8.	Start-up meeting	15

3.9.	Licensee request to start-up	15

3.10.	Maintenance schedule exceptions list	15

3.11.	Return to service justification	15

3.12.	Graphite core inspections	15

3.13.	Appointed examiner statement – concrete pre-stressed pressure vessel	16

3.14.	Appointed examiner statement – reactor penetrations examination	16

3.15.	Appointed examiner statement – PSSR	16

3.16.	Independent nuclear safety	16

3.17.	Civil nuclear security	17

3.18.	Engagement with other governmental agencies	17

4.	Matters arising from ONR’s work	17

5.	Conclusions	17

6.	Recommendations	18

References	19

# Permission requested

EDF Energy Nuclear Generation Limited (the licensee) has asked for our consent to start-up Torness (TOR) Reactor 2 (R2) in accordance with its arrangements under Licence Condition (LC) 30, periodic shutdown.

# Background

The nuclear site licence for TOR requires the licensee to shutdown any plant or process for the purpose of Examination, Inspection, Maintenance or Testing (EIMT) in accordance with the requirements of the plant maintenance schedule (referred to in LC 28). The TOR maintenance schedule preface (an approved document under LC 28 (4)) specifies that reactor periodic shutdowns (referred to by the licensee as statutory outages) take place after a maximum period of three calendar years from consent to start-up after the previous periodic shutdown.

We gave consent to start-up R2 after its last periodic shutdown on 25 July 2022. Therefore, it was required to shutdown on or before 25 July 2025. However, in order to de-conflict the periodic shutdown programme for 2024/2025 and minimise the impact of supply chain resource availability, we gave our agreement to extend the operating period of R2 until no later than 9 February 2026.

R2 was shutdown on 19 January 2026 for its periodic shutdown (denoted as S13R2) with a planned duration of 80 days. The licensee’s outage intentions document [1] set out the organisation infrastructure and management arrangements to deliver the safety related activities being undertaken during the shutdown in accordance with the maintenance schedule, statutory inspections, modifications and significant work.

# Assessment and inspection work carried out by ONR in consideration of this request

In accordance with the regulatory permissioning strategy (PR-02211), our regulation of the TOR S13R2 periodic shutdown involved assessments and inspections by specialist inspectors and oversight by the project inspector. Our assessments and inspections have focused on confirming that:

the EIMT requirements specified in the station’s maintenance schedule in support of LC 30 have been complied with;

EIMT has been carried out by Suitably Qualified and Experienced Persons (SQEP), with an appropriate level of supervision and quality assurance in place, commensurate with the equipment’s safety function; and

safety issues identified by the licensee during the shutdown have been adequately addressed with suitable and sufficient safety justification provided to allow a regulatory judgement to be made in support of restart of the reactor.

Based on the scope of work identified in the outage intentions document, advice from the following disciplines was sought:

Graphite structural integrity

Steel structural integrity

Electrical engineering

Control and instrumentation

Mechanical engineering

Civil engineering

The assessments and inspections were undertaken in accordance with ONR technical assessment and inspection guidance. The following sections provide summaries of the findings for each technical discipline which has informed our recommendation to grant consent to start-up TOR R2.

## Graphite structural integrity

Reference [2] reports the findings of our graphite structural integrity assessment of the TOR S13R2 periodic shutdown.

The inspector considered the implications of the licensee’s fuel channel inspection results and whether they could challenge the relevant graphite safety case limits.

The scope of the licensee’s inspection activities consisted of:

visual and dimensional inspection of a 20 fuel channels;

trepanning of a minimum of 30 graphite specimens, with a target of 36 samples;

visual and dimensional inspection of one control rod channel;

inspection of three faces of the peripheral shield wall; and

inspection of six channels with the eddy current inspection tool.

The inspections found 13 full height axial cracked bricks (1 previously observed and 12 new observations). This was within the range predicted by the licensee, but higher than the central estimate. The inspector judged that this was not significant with respect to the start-up of R2, but would inform on-going engagements associated with regulatory issue RI-12467 related to confidence in the forecast of axial cracked graphite fuel brick accumulation.

The licensee’s return to service engineering change documents (EC) were not complete at the time of the assessment. Therefore, the inspector recommended that the project inspector should confirm that the Independent Nuclear Safety Assessment (INSA) statements for the return to service EC and graphite inspections EC have been made available by the licensee and are in agreement with the views in the EC’s. The project inspector has received and is content with this information (refer to section 3.12).

The inspector was content that the findings of the graphite inspections did not challenge the existing graphite safety case and had no objection to us granting consent to start-up TOR R2.

## Steel structural integrity

Reference [3] reports the findings of our steel structural integrity inspection of the TOR S13R2 periodic shutdown. The inspector targeted

Corrosion

Restraints and hangers

Reactor internal inspections

Boilers and heat exchangers, decay heat removal system, by-pass gas plant and relief systems

Flow accelerated corrosion

Steam, feed and carbon dioxide pipework

Cooling water systems

Outage assessment panel (OAP)

Weld inspections and non-destructive testing

Compliance with the Pressure Systems Safety Regulations 2000 (PSSR).

The inspector judged that findings identified through the licensee’s outage inspection programme were appropriately categorised, assessed via the OAP, and managed in accordance with the licensee’s arrangements. The inspector was satisfied that the PSSR competent person was providing appropriate support and oversight to the licensee, in accordance with the PSSR statutory maintenance schedule and associated written schemes of examination.

The inspector judged that the licensee had undertaken sufficient inspection and assessment, from a structural integrity perspective, to demonstrate compliance with LC 28 and PSSR arrangements and did not raise any objections to us granting consent to start-up TOR R2.

## Electrical engineering

Reference [4] reports the findings of our electrical engineering inspection of the TOR S13R2 periodic shutdown.

The inspector targeted the electrical engineering structures, systems and components (SSCs) that were being maintained, and sampled the following:

Electrical engineering SSCs examination, inspection, maintenance and test schedule

Progress against the station’s reactor 2 statutory outage plan

Significant emergent electrical engineering issues, where applicable, and any resultant resolution

Completed S13R2 electrical engineering work activity documentation

Electrical engineering activity deferrals, where applicable

S13R2 statutory outage scheduled electrical engineering changes, where applicable.

The inspector conducted a walk down to sample work undertaken and to assess the condition of plant and equipment.

The inspector was satisfied with the condition of the electrical equipment observed, the management of emergent issues and completion of maintenance records. The inspector provided regulatory advice with respect to the control of access arrangements to switch rooms and operating experience on the use of temporary electrical supply cables.

The inspector was satisfied that the licensee adequately demonstrated the implementation of their arrangements for the S13R2 periodic shutdown and did not identify any issues from an electrical engineering perspective which would prevent us granting consent for R2 to return to service.

## Control and instrumentation

Reference [5] reports the findings of our control and instrumentation (C&I) inspection of the TOR S13R2 periodic shutdown.

The inspector sampled EIMT activities associated with the following C&I equipment and systems:

Reactor safety circuits;

Post trip logic equipment;

Gas circulators;

Torness online computing system;

Control rod control system;

Secondary shutdown system;

Boiler feed and water treatment systems;

In-core thermocouples; and

Diesel generators.

The inspector was satisfied that the activities sampled had been completed and based on the information provided, that the outstanding EIMT activities would be completed satisfactorily.

The inspector was content with the EC’s being implemented during the shutdown and judged that appropriate focus was being given to ageing and obsolescence equipment management.

The inspector identified some shortfalls relating to maintenance documentation and record keeping. The inspector did not consider that these posed an immediate or significant risk to nuclear safety or needed to be addressed before R2 returned to service.

The inspector did not identify any significant issues and supported us granting consent to start-up TOR R2.

## Mechanical engineering

Reference [6] reports the findings of our mechanical engineering inspection of the TOR S13R2 periodic shutdown.

The inspector targeted the following mechanical engineering SSCs, based on their contribution to nuclear safety:

Main boilers - relief valves and isolation valves

Decay heat system - relief valves and isolation valves

Gas circulators - maintenance and statutory inspections including lubricating oil systems

The inspector was satisfied that the licensee had adequately demonstrated the implementation of their arrangements for the S13R2 periodic shutdown, including inspection and observations of the actual condition of SSCs, management of emergent issues and completion of work order cards.

The inspector did not identify any issues that prevent us granting consent for R2 to return to service.

## Civil engineering

Reference [7] reports the findings of our civil engineering assessment and inspection of the TOR S13R2 periodic shutdown.

The inspector targeted the surveillances, inspections and tests of safety related components of the TOR R2 Pre-stressed Concrete Pressure Vessel (PCPV), reported in the Appointed Examiner’s (APEX) report. Specific attention was given to the concrete surface, strain gauge monitoring and main reactor coolant loss as these were carried out following the extension of the operating period of R2 until the issue of the current examination report.

The inspector was satisfied that the licensee has:

carried out inspection, testing and monitoring such that significant PCPV defects would have been identified;

adequately demonstrated that the PCPV is free from defects such that its safety function is not impaired; and

demonstrated that the civil engineering components of the PCPV have adequate margins to allow for any ageing and degradation processes for the proposed period of operation.

The inspector was satisfied that the licensee has demonstrated that the overall condition of the PCPV is satisfactory and was content to support granting consent to start-up TOR R2.

## Early outage safety review

We observed the early outage safety review [8] conducted by the licensee’s internal nuclear assurance team. The review focused on nuclear safety, including defence-in-depth arrangements, protected plant controls and the safety of personnel and plant.

The review identified examples of good practice in the following areas:

work area standards;

foreign material exclusion control;

contract partner engagement, including welfare arrangements;

Defence-in-depth governance; and

effective field leadership and constructive challenge.

Four areas for improvement were raised to address recurring themes observed during the review:

organisation of lifting operations;

implementation of defence-in-depth mitigations;

pedestrian / vehicle control; and

adherence to security standards.

In addition, three opportunities for improvement were identified associated with:

temporary barriers;

oil leak management; and

process alignment for lifting.

The TOR management team responded positively to the findings and committed to implement appropriate corrective actions.

## Start-up meeting

The licensee presented a summary of the safety and technical performance of the S13R2 periodic shutdown at the start-up meeting [9] on 12 March 2026. We advised the licensee that there were no safety issues that would prevent us granting consent to start-up of R2.

## Licensee request to start-up

The licensee has requested [10] our consent to start-up TOR R2 under LC 30 (3). The TOR station director confirmed, that with the exception of the activities required for start-up, the plant is in a satisfactory state for a further period of operation until the next scheduled periodic shutdown.

## Maintenance schedule exceptions list

The licensee has confirmed [11] that all the required maintenance scheduled examinations, inspections, maintenance and testing are complete, with the exception of work requiring the reactor to be at power, controlled under the licensee’s arrangements.

## Return to service justification

EC 376956 [12] presents the licensee’s results of the S13R2 outage inspection programme and reactor internal inspections programme. It confirms that the inspection results are acceptable, justify continuing plant reliability and assurance that no unexpected damage or degradation has been identified, or where it has been identified, that it has been suitably rectified.

The licensee's INSA [13] of EC 376956 ref considered the safety justification and supporting information, including verification records. INSA concluded that R2 is in an acceptable condition for return-to-service and subsequent period of operation to the next statutory outage.

## Graphite core inspections

EC 376959 [14] presents the licensee’s results of the R2 graphite core inspections, considers the safety significance of the observations, and justifies the return to service. It confirms that the inspection of the graphite core has been completed in accordance with the requirements of the outage intentions document and that the graphite assessment panel has confirmed that the results are within the accepted boundaries of the graphite safety case.

The licensee’s INSA [15] of EC 376959 focused on the interpretation of the inspection results against the extant safety case and the implications relating to brick segment bowing. No comments were raised, and INSA supported continued operation of R2.

## Appointed examiner statement – concrete pre-stressed pressure vessel

The appointed examiner has confirmed [16] that the required maintenance schedule inspections for the PCPV have been completed and that it is in satisfactory condition for continued operation, subject to normal in-service surveillance, until the next scheduled statutory outage, due in 2029.

## Appointed examiner statement – reactor penetrations examination

The licensee has reported the outcome of the TOR R2 PCPV penetrations thorough examination [17], required by the PSSR written scheme of examination. The penetrations were assessed as being in a satisfactory condition, with no significant challenges to integrity identified.

## Appointed examiner statement – PSSR

The licensee has submitted a statement [18] with respect to the inspections performed in accordance with PSSR during the shutdown from their independent third party PSSR competent person  (Bureau Veritas). The statement confirms that there are no changes to the plant operating conditions or reductions in inspection intervals as referenced in the written schemes of examinations.

## Independent nuclear safety

The licensee’s Independent Nuclear Assurance (INA) have maintained oversight of the periodic shutdown through their concurrence process. INA will issue a concurrence statement when they are satisfied that the outage activities have been conducted and, so far as can be established, the risks associated with start-up and continued operation are acceptable and ALARP.

INA have confirmed [19] that there are no issues that present a threat to start-up or continued operation, noting that the concurrence statement cannot be issued until work requiring the reactor to be at full power has been completed. The licensee’s arrangements provide a suitable hold-point in the start-up process to confirm the concurrence statement has been provided.

## Civil nuclear security

Our civil nuclear security site inspector has been consulted, to understand if there were any aspects of the periodic shutdown that may have an impact on the decision to grant consent to start-up TOR R2. The inspector [20] has not identified any issues that would impact on the decision to grant consent to start-up TOR R2.

## Engagement with other governmental agencies

Before issuing a Licence Instrument it is established practice to notify other competent regulatory authorities of our intentions to ensure that there are no specific objections that may compromise other regulatory requirements. The Scottish Environment Protection Agency (SEPA) were informed that we intended to grant consent to the restart of TOR R2. SEPA confirmed [21] that replacement of the by-pass gas plant cooler and work on the unit 2 SF6 Gas console have reached a satisfactory state and they have no objections to the consent.

# Matters arising from ONR’s work

There are no outstanding matters arising from our assessment and inspection activities.

# Conclusions

Based on the evidence gathered, we are satisfied that:

the EIMT requirements specified in the maintenance schedule in support of LC30 have been complied with;

the EIMT has been carried out by SQEPs, with an appropriate level of supervision and quality assurance commensurate with the equipment’s safety function; and

safety issues identified by the licensee during the shutdown have been adequately addressed with suitable and sufficient safety justification that the relevant safety case limits and conditions are not challenged.

We are content that all necessary work has been completed, subject to those activities that must be delayed until the reactor is pressurised or will be carried out during the restart. The remaining information will be reported to ONR in the 28-day report, or in specific documents that are not required prior to granting consent.

In conclusion, we have not identified any matters that would prevent us granting consent for TOR R2 to start-up after the S13R2 periodic shutdown.

# Recommendations

We should issue licence instrument 569 under LC 30 for nuclear site licence number Sc.14, granting consent to start-up Torness reactor 2.

# References

| [1] | Torness, Outage Intentions Document Unit 2 Statutory Outage 2026 S13R2, TOR/OM/S13R2/04, June 2025. ONRW-2019369590-23192. |
| --- | --- |
| [2] | ONR Assessment Report, Structural Integrity Assessment of the Graphite Core Inspection Findings, AR-01878. ONRW-2126615823-11989. |
| [3] | ONR Inspection Report, Torness R2 Outage Compliance Inspection (return to service) - Structural Integrity, IR-54272. |
| [4] | ONR Inspection Report, Torness R2 Outage Compliance Inspection (return to service) - Electrical Engineering, IR-54281. |
| [5] | ONR Inspection Report, Torness R2 Outage Compliance Inspection (return to service) - C&I, IR-54307. |
| [6] | ONR Inspection Report, Torness R2 Outage Compliance Inspection (return to service) - Mechanical Engineering, IR-54280. |
| [7] | ONR Assessment Report, Civil Engineering Assessment of the Torness Reactor 2 Pre-stressed Concrete Pressure Vessel in Support of Return to Service, AR-01905. ONRW-2126615823-12133. |
| [8] | ONR Contact Record, Torness early outage safety review, CR-03994. |
| [9] | Torness Power Station, 2026 R2 Start-Up Meeting – Minutes, 12th March 2026. ONRW-2019369590-27437. |
| [10] | Letter - Request for consent to start-up reactor 2 following 2026 periodic shutdown - NSL/TOR/50815 - 10 April 2026. ONRW-2019369590-27892. |
| [11] | MITS exemption list for S13R2 Return to Service. ONRW-2019369590-27863. |
| [12] | Return to service EC to collate the results of inspections - Torness reactor 2 statutory outage 2026 S13R2, EC 376956. ONRW-2019369590-27889. |
| [13] | INSA Approval Statement - Return to service EC to collate the results of inspections - Torness reactor 2 statutory outage 2026 S13R2, EC 376956. ONRW-2019369590-27890. |
| [14] | TOR S13R2 - Justification for Return to Service of Torness Reactor 2 Following the Graphite Core Inspections at the 2026 Periodic Shutdown - EC 376959. ONRW-2019369590-27553. |
| [15] | TOR S13R2 - INSA Approval Statement - Justification for Return to Service of Torness Reactor 2 Following the Graphite Core Inspections at the 2026 Periodic Shutdown - EC 376959. ONRW-2019369590-27554. |
| [16] | TOR S13R2 - Appointed examiner statement - concrete pre-stressed pressure vessel. ONRW-2019369590-27488. |
| [17] | TOR S13R2 - Torness Reactor 2 PCPV Penetrations PSSR Thorough Examination, E/TSK/TOR/17716/19.06, 27 March 2026. ONRW-2019369590-27633. |
| [18] | Appointed Examiner Statement - Torness Reactor 2 - 2026 Statutory Outage S13R2 Pressure System Safety Regulations - Bureau Veritas Letter 09 April 2026. ONRW-2019369590-27842. |
| [19] | TOR S13R2 - INA S13R2 Interim Start-up Memo. ONRW-2019369590-27632. |
| [20] | ONR security inspectors advice on Torness Reactor 2 periodic shutdown S13R2 - notice of no objection - email dated 26 February 2026. ONRW-2019369590-26952. |
| [21] | Scottish Environment Protection Agency advice on Torness reactor 2 periodic shutdown S13R2 - notice of no objection - email dated 23 March 2026. ONRW-2019369590-27485. |